## Data Flows
Site Name | [5 empty] | Data Flows
Note: The naming convention for the connection names is of form [Server] to [Client], as that is the normal flow of status information. Inputs flow from the server to the client, and outputs flow from the client to the server.
Connection | Version | Last Updated | Instance Count | From | To | Protocol | Baud | Client Device Name | Client Port | Client Address | Client IP Address | Server Device Name | Server Port | Server Address | Server IP Address

## PPC to RTU-1
Site Name | [5 empty] | DNP3.0 |  |  | PPC to RTU
Last updated |  | 2025-04-08 | Device Type | PPC |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | PPC
List Index | Availability | Object | Point Description | Data Type | DNP index | Bit | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Avaiable | Analog input | Global_horizontal_irradiance_W_m2 | 16-bit signed integer | 18 | [5 empty] | W/m² | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | AI_0018_Global_horizontal_irradiance_W_m2_W_per_m²
2 | Avaiable | Analog input | Average_plant_atmospheric_pressure_bar | 16-bit signed integer | 19 | [5 empty] | bar | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0019_Average_plant_atmospheric_pressure_bar_bar
3 | Avaiable | Analog input | Average_plant_temperature_degC | 16-bit signed integer | 20 | [5 empty] | °C | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0020_Average_plant_temperature_degC_°C
4 | Avaiable | Analog input | Max_gen_limit_feedback_MW | 16-bit signed integer | 21 | [5 empty] | MW | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0021_Max_gen_limit_feedback_MW_MW
5 | Avaiable | Analog input | Potential_power_MW | 16-bit signed integer | 22 | [5 empty] | MW | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0022_Potential_power_MW_MW
6 | Avaiable | Analog input | Global_horizontal_irradiance_W_m2 | 16-bit signed integer | 23 | [5 empty] | W/m² | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | AI_0023_Global_horizontal_irradiance_W_m2_W_per_m²
7 | Avaiable | Analog input | Average_plant_atmospheric_pressure_bar | 16-bit signed integer | 24 | [5 empty] | bar | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0024_Average_plant_atmospheric_pressure_bar_bar
8 | Avaiable | Analog input | Average_plant_temperature_degC | 16-bit signed integer | 25 | [5 empty] | °C | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0025_Average_plant_temperature_degC_°C
9 | Avaiable | Analog input | Max_gen_limit_feedback_MW | 16-bit signed integer | 26 | [5 empty] | MW | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0026_Max_gen_limit_feedback_MW_MW
10 | Avaiable | Analog input | Potential_power_MW | 16-bit signed integer | 27 | [5 empty] | MW | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | AI_0027_Potential_power_MW_MW

## Inverters to PPC - SG3600
Site Name | [5 empty] | Modbus |  |  |  | Inverters to PPC
Last updated |  | 2025-04-08 | Device Type | Sungrow SG3600UD | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 5 | Subsystem / Zone | Inverters
Device Register Base |  | 1 | [7 empty] | CAUTION: Sungrow device uses multiple endian conventions on a per-register basis. Consult sungrow manual for endian convention rubric.
Register Digits |  | 6
List Index | Availability | Modbus Table | Point Description | Data Type | Ignition Modbus index | Modbus Bit | Modbus Register | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Not Imported | Input Register | Protocol Number | 32-bit unsigned integer | 14999 |  | 315000 |  |  |  |  | unitless |  | 0 | 4294967295 | [6 empty] | IREG_14999_Protocol_Number |  | This point is not mapped to ignition
2 | Not Imported | Input Register | Protocol Version | 32-bit unsigned integer | 15001 |  | 315002 |  |  |  |  | unitless |  | 0 | 4294967295 | [6 empty] | IREG_15001_Protocol_Version |  | This point is not mapped to ignition
3 | Not Imported | Input Register | Serial Number | String | 15003 |  | 315004 | [14 empty] | IREG_15003_Serial_Number |  | This point is not mapped to ignition
4 | Not Imported | Input Register | Machine Type | String | 15011 |  | 315012 | [14 empty] | IREG_15011_Machine_Type |  | This point is not mapped to ignition
5 | Available | Input Register | U1 DC input #1 | 16-bit signed integer | 15029 |  | 315030 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15029_U1_DC_input_1_A
6 | Available | Input Register | U1 DC input #2 | 16-bit signed integer | 15030 |  | 315031 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15030_U1_DC_input_2_A
7 | Available | Input Register | U1 DC input #3 | 16-bit signed integer | 15031 |  | 315032 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15031_U1_DC_input_3_A
8 | Available | Input Register | U1 DC input #4 | 16-bit signed integer | 15032 |  | 315033 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15032_U1_DC_input_4_A
9 | Available | Input Register | U1 DC input #5 | 16-bit signed integer | 15033 |  | 315034 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15033_U1_DC_input_5_A
10 | Available | Input Register | U1 DC input #6 | 16-bit signed integer | 15034 |  | 315035 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15034_U1_DC_input_6_A
11 | Available | Input Register | U1 DC input #7 | 16-bit signed integer | 15035 |  | 315036 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15035_U1_DC_input_7_A
12 | Available | Input Register | U1 DC input #8 | 16-bit signed integer | 15036 |  | 315037 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15036_U1_DC_input_8_A
13 | Available | Input Register | U1 DC input #9 | 16-bit signed integer | 15037 |  | 315038 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15037_U1_DC_input_9_A
14 | Available | Input Register | U1 DC input #10 | 16-bit signed integer | 15038 |  | 315039 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15038_U1_DC_input_10_A
15 | Available | Input Register | U1 DC input #11 | 16-bit signed integer | 15039 |  | 315040 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15039_U1_DC_input_11_A
16 | Available | Input Register | U1 DC input #12 | 16-bit signed integer | 15040 |  | 315041 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15040_U1_DC_input_12_A
17 | Available | Input Register | U1 DC input #13 | 16-bit signed integer | 15041 |  | 315042 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15041_U1_DC_input_13_A
18 | Available | Input Register | U1 DC input #14 | 16-bit signed integer | 15042 |  | 315043 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15042_U1_DC_input_14_A
19 | Available | Input Register | U1 DC input #15 | 16-bit signed integer | 15043 |  | 315044 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15043_U1_DC_input_15_A
20 | Available | Input Register | U1 DC input #16 | 16-bit signed integer | 15044 |  | 315045 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15044_U1_DC_input_16_A
21 | Available | Input Register | U2 DC input #1 | 16-bit signed integer | 15047 |  | 315048 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15047_U2_DC_input_1_A
22 | Available | Input Register | U2 DC input #2 | 16-bit signed integer | 15048 |  | 315049 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15048_U2_DC_input_2_A
23 | Available | Input Register | U2 DC input #3 | 16-bit signed integer | 15049 |  | 315050 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15049_U2_DC_input_3_A
24 | Available | Input Register | U2 DC input #4 | 16-bit signed integer | 15050 |  | 315051 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15050_U2_DC_input_4_A
25 | Available | Input Register | U2 DC input #5 | 16-bit signed integer | 15051 |  | 315052 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15051_U2_DC_input_5_A
26 | Available | Input Register | U2 DC input #6 | 16-bit signed integer | 15052 |  | 315053 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15052_U2_DC_input_6_A
27 | Available | Input Register | U2 DC input #7 | 16-bit signed integer | 15053 |  | 315054 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15053_U2_DC_input_7_A
28 | Available | Input Register | U2 DC input #8 | 16-bit signed integer | 15054 |  | 315055 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15054_U2_DC_input_8_A
29 | Available | Input Register | U2 DC input #9 | 16-bit signed integer | 15055 |  | 315056 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15055_U2_DC_input_9_A
30 | Available | Input Register | U2 DC input #10 | 16-bit signed integer | 15056 |  | 315057 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15056_U2_DC_input_10_A
31 | Available | Input Register | U2 DC input #11 | 16-bit signed integer | 15057 |  | 315058 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15057_U2_DC_input_11_A
32 | Available | Input Register | U2 DC input #12 | 16-bit signed integer | 15058 |  | 315059 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15058_U2_DC_input_12_A
33 | Available | Input Register | U2 DC input #13 | 16-bit signed integer | 15059 |  | 315060 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15059_U2_DC_input_13_A
34 | Available | Input Register | U2 DC input #14 | 16-bit signed integer | 15060 |  | 315061 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15060_U2_DC_input_14_A
35 | Available | Input Register | U2 DC input #15 | 16-bit signed integer | 15061 |  | 315062 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15061_U2_DC_input_15_A
36 | Available | Input Register | U2 DC input #16 | 16-bit signed integer | 15062 |  | 315063 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15062_U2_DC_input_16_A
37 | Not Imported | Input Register | Device Type Code | 16-bit unsigned integer | 15069 |  | 315070 |  |  |  |  | unitless |  | 0 | 65535 | [6 empty] | IREG_15069_Device_Type_Code |  | This point is not mapped to ignition
38 | Not Imported | Input Register | Rated active power | 16-bit unsigned integer | 15070 |  | 315071 |  |  |  |  | kW | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15070_Rated_active_power_kW |  | This point is not mapped to ignition
39 | Available | Input Register | Daily Power yield | 32-bit unsigned integer | 15072 |  | 315073 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15072_Daily_Power_yield_kWh
40 | Available | Input Register | Monthly Power yield | 32-bit unsigned integer | 15074 |  | 315075 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15074_Monthly_Power_yield_kWh |  | This point is not mapped to ignition
41 | Available | Input Register | Total Power yield | 32-bit unsigned integer | 15076 |  | 315077 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15076_Total_Power_yield_kWh
42 | Available | Input Register | CO2 emission reduction | 32-bit unsigned integer | 15078 |  | 315079 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15078_CO2_emission_reduction_kg |  | This point is not mapped to ignition
43 | Available | Input Register | Daily grid connected minutes | 16-bit unsigned integer | 15080 |  | 315081 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15080_Daily_grid_connected_minutes_min |  | This point is not mapped to ignition
44 | Available | Input Register | Total Running Hours | 32-bit unsigned integer | 15081 |  | 315082 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15081_Total_Running_Hours_hr
45 | Available | Input Register | Total DC Power | 32-bit unsigned integer | 15091 |  | 315092 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15091_Total_DC_Power_W
46 | Available | Input Register | A-B Line Voltage | 16-bit unsigned integer | 15093 |  | 315094 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15093_A_B_Line_Voltage_V
47 | Available | Input Register | B-C Line Voltage | 16-bit unsigned integer | 15094 |  | 315095 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15094_B_C_Line_Voltage_V
48 | Available | Input Register | C-A Line Voltage | 16-bit unsigned integer | 15095 |  | 315096 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15095_C_A_Line_Voltage_V
49 | Available | Input Register | Phase A Current | 16-bit unsigned integer | 15096 |  | 315097 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15096_Phase_A_Current_A
50 | Available | Input Register | Phase B Current | 16-bit unsigned integer | 15097 |  | 315098 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15097_Phase_B_Current_A
51 | Available | Input Register | Phase C Current | 16-bit unsigned integer | 15098 |  | 315099 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15098_Phase_C_Current_A
52 | Available | Input Register | Total active power | 32-bit unsigned integer | 15099 |  | 315100 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15099_Total_active_power_W
53 | Available | Input Register | Total reactive power | 32-bit signed integer | 15101 |  | 315102 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15101_Total_reactive_power_var
54 | Available | Input Register | Total appearant power | 32-bit unsigned integer | 15103 |  | 315104 |  |  |  |  | VA | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15103_Total_appearant_power_VA |  | This point is not mapped to ignition
55 | Available | Input Register | Power Factor | 16-bit signed integer | 15105 |  | 315106 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15105_Power_Factor_PU
56 | Available | Input Register | Frequency | 16-bit unsigned integer | 15106 |  | 315107 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15106_Frequency_Hz
57 | Not Imported | Input Register | Rated reactive power | 16-bit unsigned integer | 15107 |  | 315108 |  |  |  |  | kvar | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15107_Rated_reactive_power_kvar |  | This point is not mapped to ignition
58 | Available | Input Register | Power limit actual value feedback | 32-bit unsigned integer | 15108 |  | 315109 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15108_Power_limit_actual_value_feedback_W
59 | Available | Input Register | Reactive power adjustment actual value feedback | 32-bit signed integer | 15110 |  | 315111 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15110_Reactive_power_adjustment_actual_value_feedback_var
60 | Available | Input Register | Power factor feedback | 16-bit signed integer | 15112 |  | 315113 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15112_Power_factor_feedback_PU
61 | Available | Input Register | Transformer node state | 16-bit bitfield | 15113 |  | 315114 |  |  |  |  | unitless | [9 empty] | IREG_15113_Transformer_node_state
62 | Available | Input Register | Transformer gas buildup trip | Boolean | 15113 | 0 | 315114.0 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_gas_buildup_trip
63 | Available | Input Register | Transformer gas buildup alarm | Boolean | 15113 | 1 | 315114.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_gas_buildup_alarm
64 | Available | Input Register | Transformer oil temperature alarm | Boolean | 15113 | 2 | 315114.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_oil_temperature_alarm
65 | Available | Input Register | Transformer oil temperature trip | Boolean | 15113 | 3 | 315114.3 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_oil_temperature_trip
66 | Available | Input Register | Transformer low oil level trip | Boolean | 15113 | 4 | 315114.4 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_low_oil_level_trip
67 | Available | Input Register | Transformer low oil level alarm | Boolean | 15113 | 5 | 315114.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_low_oil_level_alarm
68 | Available | Input Register | Transformer pressure relief valve trip | Boolean | 15113 | 6 | 315114.6 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_pressure_relief_valve_trip
69 | Available | Input Register | Transformer pressure relief valve alarm | Boolean | 15113 | 7 | 315114.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_pressure_relief_valve_alarm
70 | Available | Input Register | U1 load switch status | Boolean | 15113 | 8 | 315114.8 |  | None | Open | Closed | [10 empty] | IREG_15113_U1_load_switch_status
71 | Available | Input Register | U2 load switch status | Boolean | 15113 | 9 | 315114.9 |  | None | Open | Closed | [10 empty] | IREG_15113_U2_load_switch_status
72 | Available | Input Register | Circuit breaker status | Boolean | 15113 | 10 | 315114.10 |  | None | Open | Closed | [10 empty] | IREG_15113_Circuit_breaker_status
73 | Available | Input Register | Disconnector status | Boolean | 15113 | 11 | 315114.11 |  | None | Open | Closed | [10 empty] | IREG_15113_Disconnector_status
74 | Available | Input Register | Overcurrent protection trip | Boolean | 15113 | 12 | 315114.12 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Overcurrent_protection_trip
75 | Available | Input Register | Transformer high oil level alarm | Boolean | 15113 | 13 | 315114.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_high_oil_level_alarm
76 | Available | Input Register | Annual power yields | 32-bit unsigned integer | 15114 |  | 315115 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15114_Annual_power_yields_kWh |  | This point is not mapped to ignition
77 | Available | Input Register | Overall work state | 32-bit bitfield | 15116 |  | 315117 |  |  |  |  | unitless | [9 empty] | IREG_15116_Overall_work_state
78 | Available | Input Register | Running | Boolean | 15116 | 0 | 315117.0 |  | None | Running | Not Running | [10 empty] | IREG_15116_Running
79 | Available | Input Register | Stopped | Boolean | 15116 | 1 | 315117.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15116_Stopped
80 | Available | Input Register | External emergency stop overall work state | Boolean | 15116 | 2 | 315117.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_External_emergency_stop_overall_work_state
81 | Available | Input Register | Remote emergency stop | Boolean | 15116 | 3 | 315117.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_Remote_emergency_stop
82 | Available | Input Register | Door opening protection | Boolean | 15116 | 4 | 315117.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_Door_opening_protection
83 | Available | Input Register | Smoke alarm trip | Boolean | 15116 | 5 | 315117.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_Smoke_alarm_trip
84 | Available | Input Register | Local emergency stop | Boolean | 15116 | 6 | 315117.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_Local_emergency_stop
85 | Available | Input Register | Transformer oil temperature | 16-bit signed integer | 15118 |  | 315119 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15118_Transformer_oil_temperature_degC
86 | Available | Input Register | Winding temperature | 16-bit signed integer | 15119 |  | 315120 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15119_Winding_temperature_degC
87 | Available | Input Register | MV Node State 1 | 16-bit bitfield | 15125 |  | 315126 |  |  |  |  | unitless | [9 empty] | IREG_15125_MV_Node_State_1
88 | Available | Input Register | HV compartment door open alarm | Boolean | 15125 | 6 | 315126.6 |  | Off (0) | Closed | Open | [10 empty] | IREG_15125_HV_compartment_door_open_alarm
89 | Available | Input Register | SF6 low pressure alarm | Boolean | 15125 | 10 | 315126.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_SF6_low_pressure_alarm
90 | Available | Input Register | External emergency stop mv node state | Boolean | 15125 | 11 | 315126.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_External_emergency_stop_mv_node_state
91 | Available | Input Register | MV fuse blown alarm | Boolean | 15125 | 12 | 315126.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_MV_fuse_blown_alarm
92 | Available | Input Register | HV compartment smoke alarm | Boolean | 15125 | 13 | 315126.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_HV_compartment_smoke_alarm
93 | Available | Input Register | HV Local remote switch status | Boolean | 15125 | 14 | 315126.14 |  | On (1) | Local | Remote | [10 empty] | IREG_15125_HV_Local_remote_switch_status
94 | Available | Input Register | Overall alarm state | 16-bit bitfield | 15126 |  | 315127 |  |  |  |  | unitless | [9 empty] | IREG_15126_Overall_alarm_state
95 | Available | Input Register | Smoke sensor abnormal alarm | Boolean | 15126 | 0 | 315127.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15126_Smoke_sensor_abnormal_alarm
96 | Available | Input Register | Temperature sensor abnormal alarm | Boolean | 15126 | 3 | 315127.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15126_Temperature_sensor_abnormal_alarm
97 | Available | Input Register | Digital input state | 32-bit bitfield | 15128 |  | 315129 |  |  |  |  | unitless | [9 empty] | IREG_15128_Digital_input_state
98 | Available | Input Register | DI1 status | Boolean | 15128 | 0 | 315129.0 |  | None | On | Off | [10 empty] | IREG_15128_DI1_status
99 | Available | Input Register | DI2 status | Boolean | 15128 | 1 | 315129.1 |  | None | Off | On | [10 empty] | IREG_15128_DI2_status
100 | Available | Input Register | DI3 status | Boolean | 15128 | 2 | 315129.2 |  | None | Off | On | [10 empty] | IREG_15128_DI3_status
101 | Available | Input Register | DI4 status | Boolean | 15128 | 3 | 315129.3 |  | None | Off | On | [10 empty] | IREG_15128_DI4_status
102 | Available | Input Register | DI5 status | Boolean | 15128 | 4 | 315129.4 |  | None | On | Off | [10 empty] | IREG_15128_DI5_status
103 | Available | Input Register | DI6 status | Boolean | 15128 | 5 | 315129.5 |  | None | On | Off | [10 empty] | IREG_15128_DI6_status
104 | Available | Input Register | DI7 status | Boolean | 15128 | 6 | 315129.6 |  | None | On | Off | [10 empty] | IREG_15128_DI7_status
105 | Available | Input Register | DI8 status | Boolean | 15128 | 7 | 315129.7 |  | None | On | Off | [10 empty] | IREG_15128_DI8_status
106 | Available | Input Register | DI9 status | Boolean | 15128 | 8 | 315129.8 |  | None | On | Off | [10 empty] | IREG_15128_DI9_status
107 | Available | Input Register | DI10 status | Boolean | 15128 | 9 | 315129.9 |  | None | On | Off | [10 empty] | IREG_15128_DI10_status
108 | Available | Input Register | DI11 status | Boolean | 15128 | 10 | 315129.10 |  | None | On | Off | [10 empty] | IREG_15128_DI11_status
109 | Available | Input Register | DI12 status | Boolean | 15128 | 11 | 315129.11 |  | None | On | Off | [10 empty] | IREG_15128_DI12_status
110 | Available | Input Register | DI13 status | Boolean | 15128 | 12 | 315129.12 |  | None | On | Off | [10 empty] | IREG_15128_DI13_status
111 | Available | Input Register | DI14 status | Boolean | 15128 | 13 | 315129.13 |  | None | On | Off | [10 empty] | IREG_15128_DI14_status
112 | Available | Input Register | DI15 status | Boolean | 15128 | 14 | 315129.14 |  | None | On | Off | [10 empty] | IREG_15128_DI15_status
113 | Available | Input Register | DI16 status | Boolean | 15128 | 15 | 315129.15 |  | None | On | Off | [10 empty] | IREG_15128_DI16_status
114 | Available | Input Register | DI17 status | Boolean | 15128 | 16 | 315129.16 |  | None | On | Off | [10 empty] | IREG_15128_DI17_status
115 | Available | Input Register | DI18 status | Boolean | 15128 | 17 | 315129.17 |  | None | On | Off | [10 empty] | IREG_15128_DI18_status
116 | Available | Input Register | DI19 status | Boolean | 15128 | 18 | 315129.18 |  | None | On | Off | [10 empty] | IREG_15128_DI19_status
117 | Available | Input Register | DI20 status | Boolean | 15128 | 19 | 315129.19 |  | None | On | Off | [10 empty] | IREG_15128_DI20_status
118 | Available | Input Register | DI21 status | Boolean | 15128 | 20 | 315129.20 |  | None | On | Off | [10 empty] | IREG_15128_DI21_status
119 | Available | Input Register | MV Node state 2 | 32-bit bitfield | 15130 |  | 315131 |  |  |  |  | unitless | [9 empty] | IREG_15130_MV_Node_state_2
120 | Available | Input Register | MV load switch status | Boolean | 15130 | 0 | 315131.0 |  | None | Closed | Open | [10 empty] | IREG_15130_MV_load_switch_status
121 | Available | Input Register | HV remote trip | Boolean | 15130 | 1 | 315131.1 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15130_HV_remote_trip
122 | Available | Input Register | Transformer compartment door | Boolean | 15130 | 7 | 315131.7 |  | Off (0) | Closed | Open | [10 empty] | IREG_15130_Transformer_compartment_door
123 | Available | Input Register | Transformer compartment smoke alarm | Boolean | 15130 | 8 | 315131.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15130_Transformer_compartment_smoke_alarm
124 | Available | Input Register | UPS fault | Boolean | 15130 | 9 | 315131.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15130_UPS_fault
125 | Available | Input Register | U1 Daily power yield | 32-bit unsigned integer | 15149 |  | 315150 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15149_U1_Daily_power_yield_kWh
126 | Available | Input Register | U1 Monthly power yield | 32-bit unsigned integer | 15151 |  | 315152 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15151_U1_Monthly_power_yield_kWh |  | This point is not mapped to ignition
127 | Available | Input Register | U1 Total power yield | 32-bit unsigned integer | 15153 |  | 315154 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15153_U1_Total_power_yield_kWh
128 | Available | Input Register | U1 Daily grid connected minutes | 16-bit unsigned integer | 15155 |  | 315156 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15155_U1_Daily_grid_connected_minutes_min
129 | Available | Input Register | U1 Total running hours | 32-bit unsigned integer | 15156 |  | 315157 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15156_U1_Total_running_hours_hr
130 | Available | Input Register | U1 Internal Module Temperature | 16-bit signed integer | 15158 |  | 315159 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15158_U1_Internal_Module_Temperature_degC
131 | Available | Input Register | U1 DC Voltage | 16-bit unsigned integer | 15159 |  | 315160 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15159_U1_DC_Voltage_V
132 | Available | Input Register | U1 DC Current | 16-bit unsigned integer | 15160 |  | 315161 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15160_U1_DC_Current_A
133 | Available | Input Register | U1 DC Power | 32-bit unsigned integer | 15161 |  | 315162 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15161_U1_DC_Power_W
134 | Available | Input Register | U1 Voltage A-B | 16-bit unsigned integer | 15163 |  | 315164 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15163_U1_Voltage_A_B_V
135 | Available | Input Register | U1 Voltage B-C | 16-bit unsigned integer | 15164 |  | 315165 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15164_U1_Voltage_B_C_V
136 | Available | Input Register | U1 Voltage C-A | 16-bit unsigned integer | 15165 |  | 315166 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15165_U1_Voltage_C_A_V
137 | Available | Input Register | U1 Phase A Current | 16-bit unsigned integer | 15166 |  | 315167 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15166_U1_Phase_A_Current_A
138 | Available | Input Register | U1 Phase B Current | 16-bit unsigned integer | 15167 |  | 315168 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15167_U1_Phase_B_Current_A
139 | Available | Input Register | U1 Phase C Current | 16-bit unsigned integer | 15168 |  | 315169 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15168_U1_Phase_C_Current_A
140 | Available | Input Register | U1 Active Power | 32-bit unsigned integer | 15169 |  | 315170 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15169_U1_Active_Power_W
141 | Available | Input Register | U1 Reactive Power | 32-bit signed integer | 15171 |  | 315172 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15171_U1_Reactive_Power_var
142 | Available | Input Register | U1 Power Factor | 16-bit signed integer | 15173 |  | 315174 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15173_U1_Power_Factor_PU
143 | Available | Input Register | U1 Frequency | 16-bit unsigned integer | 15174 |  | 315175 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15174_U1_Frequency_Hz
144 | Available | Input Register | U1 Efficiency | 16-bit unsigned integer | 15175 |  | 315176 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15175_U1_Efficiency_pct
145 | Available | Input Register | U1 Clock Year | 16-bit unsigned integer | 15177 |  | 315178 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15177_U1_Clock_Year_year |  | This point is not mapped to ignition
146 | Available | Input Register | U1 Clock Month | 16-bit unsigned integer | 15178 |  | 315179 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15178_U1_Clock_Month_month |  | This point is not mapped to ignition
147 | Available | Input Register | U1 Clock Day | 16-bit unsigned integer | 15179 |  | 315180 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15179_U1_Clock_Day_day |  | This point is not mapped to ignition
148 | Available | Input Register | U1 Clock Hour | 16-bit unsigned integer | 15180 |  | 315181 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15180_U1_Clock_Hour_hr |  | This point is not mapped to ignition
149 | Available | Input Register | U1 Clock Minute | 16-bit unsigned integer | 15181 |  | 315182 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15181_U1_Clock_Minute_min |  | This point is not mapped to ignition
150 | Available | Input Register | U1 Clock Second | 16-bit unsigned integer | 15182 |  | 315183 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15182_U1_Clock_Second_s |  | This point is not mapped to ignition
151 | Available | Input Register | U1 Fault State 1 | 32-bit bitfield | 15185 |  | 315186 |  |  |  |  | unitless | [9 empty] | IREG_15185_U1_Fault_State_1
152 | Available | Input Register | U1 DC undervoltage alarm | Boolean | 15185 | 0 | 315186.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_undervoltage_alarm
153 | Available | Input Register | U1 DC overvoltage alarm | Boolean | 15185 | 1 | 315186.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_overvoltage_alarm
154 | Available | Input Register | U1 AC undervoltage alarm | Boolean | 15185 | 2 | 315186.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_undervoltage_alarm
155 | Available | Input Register | U1 AC overvoltage alarm | Boolean | 15185 | 3 | 315186.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_overvoltage_alarm
156 | Available | Input Register | U1 Underfrequency alarm | Boolean | 15185 | 4 | 315186.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Underfrequency_alarm
157 | Available | Input Register | U1 Overfrequency alarm | Boolean | 15185 | 5 | 315186.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Overfrequency_alarm
158 | Available | Input Register | U1 Contactor fault | Boolean | 15185 | 6 | 315186.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Contactor_fault
159 | Available | Input Register | U1 Anti islanding protection active | Boolean | 15185 | 7 | 315186.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Anti_islanding_protection_active
160 | Available | Input Register | U1 Sensor failure | Boolean | 15185 | 8 | 315186.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Sensor_failure
161 | Available | Input Register | U1 PDP protection active | Boolean | 15185 | 9 | 315186.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_PDP_protection_active
162 | Available | Input Register | U1 Module overtemperature alarm | Boolean | 15185 | 10 | 315186.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Module_overtemperature_alarm
163 | Available | Input Register | U1 Reactor overtemperature alarm | Boolean | 15185 | 11 | 315186.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Reactor_overtemperature_alarm
164 | Available | Input Register | U1 Transformer overtemperature alarm | Boolean | 15185 | 12 | 315186.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Transformer_overtemperature_alarm
165 | Available | Input Register | U1 DC leakage current protection alarm | Boolean | 15185 | 13 | 315186.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_leakage_current_protection_alarm
166 | Available | Input Register | U1 AC leakage current protection alarm | Boolean | 15185 | 14 | 315186.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_leakage_current_protection_alarm
167 | Available | Input Register | U1 Overload protection active | Boolean | 15185 | 15 | 315186.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Overload_protection_active
168 | Available | Input Register | U1 GFDI protection active | Boolean | 15185 | 17 | 315186.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_GFDI_protection_active
169 | Available | Input Register | U1 Fan fault | Boolean | 15185 | 18 | 315186.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Fan_fault
170 | Available | Input Register | U1 DC fuse failure | Boolean | 15185 | 19 | 315186.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_fuse_failure
171 | Available | Input Register | U1 Detection fuse failure | Boolean | 15185 | 20 | 315186.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Detection_fuse_failure
172 | Available | Input Register | U1 DC overcurrent | Boolean | 15185 | 21 | 315186.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_overcurrent
173 | Available | Input Register | U1 AC overcurrent | Boolean | 15185 | 22 | 315186.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_overcurrent
174 | Available | Input Register | U1 Frequency abnormal | Boolean | 15185 | 23 | 315186.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Frequency_abnormal
175 | Available | Input Register | U1 Temperature abnormal | Boolean | 15185 | 24 | 315186.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Temperature_abnormal
176 | Available | Input Register | U1 Hardware fault | Boolean | 15185 | 25 | 315186.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Hardware_fault
177 | Available | Input Register | U1 Grounding fault | Boolean | 15185 | 26 | 315186.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Grounding_fault
178 | Available | Input Register | U1 Bus overvoltage | Boolean | 15185 | 27 | 315186.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Bus_overvoltage
179 | Available | Input Register | U1 Bus undervoltage | Boolean | 15185 | 28 | 315186.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Bus_undervoltage
180 | Available | Input Register | U1 Inverter overvoltage | Boolean | 15185 | 29 | 315186.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Inverter_overvoltage
181 | Available | Input Register | U1 Fault State 2 | 32-bit bitfield | 15187 |  | 315188 |  |  |  |  | unitless | [9 empty] | IREG_15187_U1_Fault_State_2
182 | Available | Input Register | U1 Insulation impedance fault | Boolean | 15187 | 0 | 315188.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Insulation_impedance_fault
183 | Available | Input Register | U1 AC SPD fault | Boolean | 15187 | 1 | 315188.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_SPD_fault
184 | Available | Input Register | U1 Sampling fault | Boolean | 15187 | 2 | 315188.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Sampling_fault
185 | Available | Input Register | U1 DC polarity reversed alarm | Boolean | 15187 | 3 | 315188.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_polarity_reversed_alarm
186 | Available | Input Register | U1 Control power supply fault | Boolean | 15187 | 4 | 315188.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Control_power_supply_fault
187 | Available | Input Register | U1 Backup power supply fault | Boolean | 15187 | 5 | 315188.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Backup_power_supply_fault
188 | Available | Input Register | U1 AC current imballance | Boolean | 15187 | 6 | 315188.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_current_imballance
189 | Available | Input Register | U1 AC fuse fault | Boolean | 15187 | 7 | 315188.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_fuse_fault
190 | Available | Input Register | U1 DC SPD fault | Boolean | 15187 | 8 | 315188.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_SPD_fault
191 | Available | Input Register | U1 Buffer contactor fault | Boolean | 15187 | 9 | 315188.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Buffer_contactor_fault
192 | Available | Input Register | U1 DC injection fault | Boolean | 15187 | 10 | 315188.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_injection_fault
193 | Available | Input Register | U1 DC switch fault | Boolean | 15187 | 11 | 315188.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_switch_fault
194 | Available | Input Register | U1 Device code repeat fault | Boolean | 15187 | 12 | 315188.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Device_code_repeat_fault
195 | Available | Input Register | U1 Parallel operation communication failure | Boolean | 15187 | 13 | 315188.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Parallel_operation_communication_failure
196 | Available | Input Register | U1 Control cabinet temperature alarm | Boolean | 15187 | 14 | 315188.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Control_cabinet_temperature_alarm
197 | Available | Input Register | U1 DC fuse grounding fault | Boolean | 15187 | 15 | 315188.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_fuse_grounding_fault
198 | Available | Input Register | U1 Reversed branch over current | Boolean | 15187 | 16 | 315188.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Reversed_branch_over_current
199 | Available | Input Register | U1 Grid voltage imballance | Boolean | 15187 | 17 | 315188.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Grid_voltage_imballance
200 | Available | Input Register | U1 AC cabinet temperature alarm | Boolean | 15187 | 20 | 315188.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_cabinet_temperature_alarm
201 | Available | Input Register | U1 AC switch disconnection | Boolean | 15187 | 21 | 315188.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_switch_disconnection
202 | Available | Input Register | U1 AC switch fault | Boolean | 15187 | 22 | 315188.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_switch_fault
203 | Available | Input Register | U1 Soft start fault | Boolean | 15187 | 23 | 315188.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Soft_start_fault
204 | Available | Input Register | U1 DC voltage sampling fault | Boolean | 15187 | 24 | 315188.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_voltage_sampling_fault
205 | Available | Input Register | U1 Fan 2 fault | Boolean | 15187 | 25 | 315188.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Fan_2_fault
206 | Available | Input Register | U1 Current unbalance 2 | Boolean | 15187 | 26 | 315188.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Current_unbalance_2
207 | Available | Input Register | U1 Current unbalance 3 | Boolean | 15187 | 27 | 315188.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Current_unbalance_3
208 | Available | Input Register | U1 Drive board fault | Boolean | 15187 | 28 | 315188.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Drive_board_fault
209 | Available | Input Register | U1 DC cabinet temperature alarm | Boolean | 15187 | 29 | 315188.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_cabinet_temperature_alarm
210 | Available | Input Register | U1 Neutral point potential shift alarm | Boolean | 15187 | 30 | 315188.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Neutral_point_potential_shift_alarm
211 | Available | Input Register | U1 Carrier sync failure | Boolean | 15187 | 31 | 315188.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Carrier_sync_failure
212 | Available | Input Register | U1 Node State 1 | 32-bit bitfield | 15193 |  | 315194 |  |  |  |  | unitless | [9 empty] | IREG_15193_U1_Node_State_1
213 | Available | Input Register | U1 AC circuit breaker status | Boolean | 15193 | 0 | 315194.0 |  | None | Closed | Open | [10 empty] | IREG_15193_U1_AC_circuit_breaker_status
214 | Available | Input Register | U1 AC main contactor status | Boolean | 15193 | 1 | 315194.1 |  | None | Closed | Open | [10 empty] | IREG_15193_U1_AC_main_contactor_status
215 | Available | Input Register | U1 ABC fault | Boolean | 15193 | 12 | 315194.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15193_U1_ABC_fault
216 | Available | Input Register | U1 ABC local remote status | Boolean | 15193 | 13 | 315194.13 |  | Off (0) | Remote | Local | [10 empty] | IREG_15193_U1_ABC_local_remote_status
217 | Available | Input Register | U1 Node State 2 | 32-bit bitfield | 15195 |  | 315196 |  |  |  |  | unitless | [9 empty] | IREG_15195_U1_Node_State_2
218 | Available | Input Register | U1 SPD status | Boolean | 15195 | 12 | 315196.12 |  | None | Closed | Open | [10 empty] | IREG_15195_U1_SPD_status
219 | Available | Input Register | U1 DC switch 1 status | Boolean | 15195 | 20 | 315196.20 |  | None | Closed | Open | [10 empty] | IREG_15195_U1_DC_switch_1_status
220 | Available | Input Register | U1 DC switch 2 status | Boolean | 15195 | 21 | 315196.21 |  | None | Closed | Open | [10 empty] | IREG_15195_U1_DC_switch_2_status
221 | Available | Input Register | U1 DC switch 3 status | Boolean | 15195 | 22 | 315196.22 |  | None | Closed | Open | [10 empty] | IREG_15195_U1_DC_switch_3_status
222 | Available | Input Register | U1 DC switch 4 status | Boolean | 15195 | 23 | 315196.23 |  | None | Closed | Open | [10 empty] | IREG_15195_U1_DC_switch_4_status
223 | Available | Input Register | U1 Temperature 1 | 16-bit signed integer | 15197 |  | 315198 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15197_U1_Temperature_1_degC
224 | Available | Input Register | U1 Temperature 2 | 16-bit signed integer | 15198 |  | 315199 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15198_U1_Temperature_2_degC
225 | Available | Input Register | U1 Temperature 3 | 16-bit signed integer | 15199 |  | 315200 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15199_U1_Temperature_3_degC
226 | Available | Input Register | U1 Temperature 4 | 16-bit signed integer | 15200 |  | 315201 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15200_U1_Temperature_4_degC
227 | Available | Input Register | U1 Temperature 5 | 16-bit signed integer | 15201 |  | 315202 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15201_U1_Temperature_5_degC
228 | Available | Input Register | U1 Temperature 6 | 16-bit signed integer | 15202 |  | 315203 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15202_U1_Temperature_6_degC
229 | Available | Input Register | U1 Positive Resistance to Ground | 32-bit unsigned integer | 15203 |  | 315204 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15203_U1_Positive_Resistance_to_Ground_kOhm
230 | Available | Input Register | U1 Negative Resistance to Ground | 32-bit unsigned integer | 15205 |  | 315206 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15205_U1_Negative_Resistance_to_Ground_kOhm
231 | Available | Input Register | U1 Work State | 32-bit bitfield | 15207 |  | 315208 |  |  |  |  | unitless | [9 empty] | IREG_15207_U1_Work_State
232 | Available | Input Register | U1 Running | Boolean | 15207 | 0 | 315208.0 |  | None | Running | Not Running | [10 empty] | IREG_15207_U1_Running
233 | Available | Input Register | U1 Stopped | Boolean | 15207 | 1 | 315208.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15207_U1_Stopped
234 | Available | Input Register | U1 Initial Standby | Boolean | 15207 | 2 | 315208.2 |  | None | Standby | Not Standby | [10 empty] | IREG_15207_U1_Initial_Standby
235 | Available | Input Register | U1 Key Stop | Boolean | 15207 | 3 | 315208.3 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15207_U1_Key_Stop
236 | Available | Input Register | U1 Standby | Boolean | 15207 | 4 | 315208.4 |  | None | Standby | Not Standby | [10 empty] | IREG_15207_U1_Standby
237 | Available | Input Register | U1 Emergency Stop | Boolean | 15207 | 5 | 315208.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Emergency_Stop
238 | Available | Input Register | U1 Starting | Boolean | 15207 | 6 | 315208.6 |  | None | Starting | Not Starting | [10 empty] | IREG_15207_U1_Starting
239 | Available | Input Register | U1 Stopping | Boolean | 15207 | 7 | 315208.7 |  | None | Stopping | Not Stopping | [10 empty] | IREG_15207_U1_Stopping
240 | Available | Input Register | U1 Fault Stop | Boolean | 15207 | 9 | 315208.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Fault_Stop
241 | Available | Input Register | U1 Alarm running | Boolean | 15207 | 10 | 315208.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Alarm_running
242 | Available | Input Register | U1 Derating running | Boolean | 15207 | 11 | 315208.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Derating_running
243 | Available | Input Register | U1 IO-DSP communication failure | Boolean | 15207 | 13 | 315208.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_IO_DSP_communication_failure
244 | Available | Input Register | U1 Inverter is running | Boolean | 15207 | 17 | 315208.17 |  | None | Running | Not Running | [10 empty] | IREG_15207_U1_Inverter_is_running
245 | Available | Input Register | U1 Inverter is stopped | Boolean | 15207 | 18 | 315208.18 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15207_U1_Inverter_is_stopped
246 | Available | Input Register | U1 Anti-PID active | Boolean | 15207 | 19 | 315208.19 |  | On (1) | Active | Not-Active | [10 empty] | IREG_15207_U1_Anti_PID_active
247 | Available | Input Register | U1 IO-MDC communication abnormal | Boolean | 15207 | 20 | 315208.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_IO_MDC_communication_abnormal
248 | Available | Input Register | U1 Alarm State | 32-bit bitfield | 15209 |  | 315210 |  |  |  |  | unitless | [9 empty] | IREG_15209_U1_Alarm_State
249 | Available | Input Register | U1 Temperature alarm | Boolean | 15209 | 0 | 315210.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Temperature_alarm
250 | Available | Input Register | U1 Low insulation resistance alarm | Boolean | 15209 | 1 | 315210.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Low_insulation_resistance_alarm
251 | Available | Input Register | U1 GFRT operation alarm | Boolean | 15209 | 2 | 315210.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_GFRT_operation_alarm
252 | Available | Input Register | U1 CT unbalance | Boolean | 15209 | 3 | 315210.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_CT_unbalance
253 | Available | Input Register | U1 DC fuse failure | Boolean | 15209 | 4 | 315210.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_fuse_failure
254 | Available | Input Register | U1 DSP-MDC communication failure | Boolean | 15209 | 5 | 315210.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DSP_MDC_communication_failure
255 | Available | Input Register | U1 DC sensor fault | Boolean | 15209 | 6 | 315210.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_sensor_fault
256 | Available | Input Register | U1 DC SPD fault | Boolean | 15209 | 7 | 315210.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_SPD_fault
257 | Available | Input Register | U1 AC SPD fault | Boolean | 15209 | 8 | 315210.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_AC_SPD_fault
258 | Available | Input Register | U1 Bypass circuit breaker fault | Boolean | 15209 | 9 | 315210.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Bypass_circuit_breaker_fault
259 | Available | Input Register | U1 Bypass fuse abnormal / branch fault | Boolean | 15209 | 10 | 315210.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Bypass_fuse_abnormal___branch_fault
260 | Available | Input Register | U1 Ground fuse fault | Boolean | 15209 | 11 | 315210.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Ground_fuse_fault
261 | Available | Input Register | U1 DC switch fault | Boolean | 15209 | 12 | 315210.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_switch_fault
262 | Available | Input Register | U1 Anti-PID power supply | Boolean | 15209 | 13 | 315210.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Anti_PID_power_supply
263 | Available | Input Register | U1 Fan fault | Boolean | 15209 | 14 | 315210.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Fan_fault
264 | Available | Input Register | U1 External power supply fault | Boolean | 15209 | 15 | 315210.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_External_power_supply_fault
265 | Available | Input Register | U1 DC bypass forward overcurrent alarm | Boolean | 15209 | 16 | 315210.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_bypass_forward_overcurrent_alarm
266 | Available | Input Register | U1 DC bypass reverse overcurrent alarm | Boolean | 15209 | 17 | 315210.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_bypass_reverse_overcurrent_alarm
267 | Available | Input Register | U1 Tributary board communication failure | Boolean | 15209 | 18 | 315210.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Tributary_board_communication_failure
268 | Available | Input Register | U1 AC circuit breaker fault | Boolean | 15209 | 19 | 315210.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_AC_circuit_breaker_fault
269 | Available | Input Register | U1 Meter communication failure | Boolean | 15209 | 20 | 315210.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Meter_communication_failure
270 | Available | Input Register | U1 Fan 2 fault | Boolean | 15209 | 21 | 315210.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Fan_2_fault
271 | Available | Input Register | U1 Contactor contact fault | Boolean | 15209 | 22 | 315210.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Contactor_contact_fault
272 | Available | Input Register | U1 Temperature and humidity sensor fault | Boolean | 15209 | 23 | 315210.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Temperature_and_humidity_sensor_fault
273 | Available | Input Register | U1 Frequency deviation active power regulation | Boolean | 15209 | 24 | 315210.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Frequency_deviation_active_power_regulation
274 | Available | Input Register | U1 Voltage deviation reactive power regulation | Boolean | 15209 | 25 | 315210.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Voltage_deviation_reactive_power_regulation
275 | Available | Input Register | U1 Insulation impedance sensor fault | Boolean | 15209 | 26 | 315210.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Insulation_impedance_sensor_fault
276 | Available | Input Register | U1 Busbar temperature alarm | Boolean | 15209 | 27 | 315210.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Busbar_temperature_alarm
277 | Available | Input Register | U1 Abnormal derating of fan | Boolean | 15209 | 28 | 315210.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Abnormal_derating_of_fan
278 | Available | Input Register | U1 Frequency abnormal | Boolean | 15209 | 30 | 315210.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Frequency_abnormal
279 | Available | Input Register | U1 Negative Voltage to Ground | 16-bit signed integer | 15211 |  | 315212 |  |  |  |  | V | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15211_U1_Negative_Voltage_to_Ground_V
280 | Available | Input Register | U1 Annual Power Yield | 32-bit unsigned integer | 15212 |  | 315213 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15212_U1_Annual_Power_Yield_kWh |  | This point is not mapped to ignition
281 | Available | Input Register | U1 CO2 Emission Reduction | 32-bit unsigned integer | 15214 |  | 315215 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15214_U1_CO2_Emission_Reduction_kg |  | This point is not mapped to ignition
282 | Available | Input Register | U2 Daily power yield | 32-bit unsigned integer | 15269 |  | 315270 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15269_U2_Daily_power_yield_kWh
283 | Available | Input Register | U2 Monthly power yield | 32-bit unsigned integer | 15271 |  | 315272 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15271_U2_Monthly_power_yield_kWh |  | This point is not mapped to ignition
284 | Available | Input Register | U2 Total power yield | 32-bit unsigned integer | 15273 |  | 315274 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15273_U2_Total_power_yield_kWh
285 | Available | Input Register | U2 Daily grid connected minutes | 16-bit unsigned integer | 15275 |  | 315276 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15275_U2_Daily_grid_connected_minutes_min
286 | Available | Input Register | U2 Total runninghours | 32-bit unsigned integer | 15276 |  | 315277 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15276_U2_Total_runninghours_hr
287 | Available | Input Register | U2 Internal Module Temperature | 16-bit signed integer | 15278 |  | 315279 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15278_U2_Internal_Module_Temperature_degC
288 | Available | Input Register | U2 DC Voltage | 16-bit unsigned integer | 15279 |  | 315280 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15279_U2_DC_Voltage_V
289 | Available | Input Register | U2 DC Current | 16-bit unsigned integer | 15280 |  | 315281 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15280_U2_DC_Current_A
290 | Available | Input Register | U2 DC Power | 32-bit unsigned integer | 15281 |  | 315282 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15281_U2_DC_Power_W
291 | Available | Input Register | U2 Voltage A-B | 16-bit unsigned integer | 15283 |  | 315284 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15283_U2_Voltage_A_B_V
292 | Available | Input Register | U2 Voltage B-C | 16-bit unsigned integer | 15284 |  | 315285 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15284_U2_Voltage_B_C_V
293 | Available | Input Register | U2 Voltage C-A | 16-bit unsigned integer | 15285 |  | 315286 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15285_U2_Voltage_C_A_V
294 | Available | Input Register | U2 Phase A Current | 16-bit unsigned integer | 15286 |  | 315287 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15286_U2_Phase_A_Current_A
295 | Available | Input Register | U2 Phase B Current | 16-bit unsigned integer | 15287 |  | 315288 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15287_U2_Phase_B_Current_A
296 | Available | Input Register | U2 Phase C Current | 16-bit unsigned integer | 15288 |  | 315289 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15288_U2_Phase_C_Current_A
297 | Available | Input Register | U2 Active Power | 32-bit unsigned integer | 15289 |  | 315290 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15289_U2_Active_Power_W
298 | Available | Input Register | U2 Reactive Power | 32-bit signed integer | 15291 |  | 315292 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15291_U2_Reactive_Power_var
299 | Available | Input Register | U2 Power Factor | 16-bit signed integer | 15293 |  | 315294 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15293_U2_Power_Factor_PU
300 | Available | Input Register | U2 Frequency | 16-bit unsigned integer | 15294 |  | 315295 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15294_U2_Frequency_Hz
301 | Available | Input Register | U2 Efficiency | 16-bit unsigned integer | 15295 |  | 315296 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15295_U2_Efficiency_pct
302 | Available | Input Register | U2 Clock Year | 16-bit unsigned integer | 15297 |  | 315298 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15297_U2_Clock_Year_year |  | This point is not mapped to ignition
303 | Available | Input Register | U2 Clock Month | 16-bit unsigned integer | 15298 |  | 315299 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15298_U2_Clock_Month_month |  | This point is not mapped to ignition
304 | Available | Input Register | U2 Clock Day | 16-bit unsigned integer | 15299 |  | 315300 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15299_U2_Clock_Day_day |  | This point is not mapped to ignition
305 | Available | Input Register | U2 Clock Hour | 16-bit unsigned integer | 15300 |  | 315301 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15300_U2_Clock_Hour_hr |  | This point is not mapped to ignition
306 | Available | Input Register | U2 Clock Minute | 16-bit unsigned integer | 15301 |  | 315302 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15301_U2_Clock_Minute_min |  | This point is not mapped to ignition
307 | Available | Input Register | U2 Clock Second | 16-bit unsigned integer | 15302 |  | 315303 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15302_U2_Clock_Second_s |  | This point is not mapped to ignition
308 | Available | Input Register | U2 Fault State 1 | 32-bit bitfield | 15305 |  | 315306 |  |  |  |  | unitless | [9 empty] | IREG_15305_U2_Fault_State_1
309 | Available | Input Register | U2 DC undervoltage alarm | Boolean | 15305 | 0 | 315306.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_undervoltage_alarm
310 | Available | Input Register | U2 DC overvoltage alarm | Boolean | 15305 | 1 | 315306.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_overvoltage_alarm
311 | Available | Input Register | U2 AC undervoltage alarm | Boolean | 15305 | 2 | 315306.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_undervoltage_alarm
312 | Available | Input Register | U2 AC overvoltage alarm | Boolean | 15305 | 3 | 315306.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_overvoltage_alarm
313 | Available | Input Register | U2 Underfrequency alarm | Boolean | 15305 | 4 | 315306.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Underfrequency_alarm
314 | Available | Input Register | U2 Overfrequency alarm | Boolean | 15305 | 5 | 315306.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Overfrequency_alarm
315 | Available | Input Register | U2 Contactor fault | Boolean | 15305 | 6 | 315306.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Contactor_fault
316 | Available | Input Register | U2 Anti islanding protection active | Boolean | 15305 | 7 | 315306.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Anti_islanding_protection_active
317 | Available | Input Register | U2 Sensor failure | Boolean | 15305 | 8 | 315306.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Sensor_failure
318 | Available | Input Register | U2 PDP protection active | Boolean | 15305 | 9 | 315306.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_PDP_protection_active
319 | Available | Input Register | U2 Module overtemperature alarm | Boolean | 15305 | 10 | 315306.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Module_overtemperature_alarm
320 | Available | Input Register | U2 Reactor overtemperature alarm | Boolean | 15305 | 11 | 315306.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Reactor_overtemperature_alarm
321 | Available | Input Register | U2 Transformer overtemperature alarm | Boolean | 15305 | 12 | 315306.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Transformer_overtemperature_alarm
322 | Available | Input Register | U2 DC leakage current protection alarm | Boolean | 15305 | 13 | 315306.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_leakage_current_protection_alarm
323 | Available | Input Register | U2 AC leakage current protection alarm | Boolean | 15305 | 14 | 315306.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_leakage_current_protection_alarm
324 | Available | Input Register | U2 Overload protection active | Boolean | 15305 | 15 | 315306.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Overload_protection_active
325 | Available | Input Register | U2 GFDI protection active | Boolean | 15305 | 17 | 315306.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_GFDI_protection_active
326 | Available | Input Register | U2 Fan fault | Boolean | 15305 | 18 | 315306.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Fan_fault
327 | Available | Input Register | U2 DC fuse failure | Boolean | 15305 | 19 | 315306.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_fuse_failure
328 | Available | Input Register | U2 Detection fuse failure | Boolean | 15305 | 20 | 315306.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Detection_fuse_failure
329 | Available | Input Register | U2 DC overcurrent | Boolean | 15305 | 21 | 315306.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_overcurrent
330 | Available | Input Register | U2 AC overcurrent | Boolean | 15305 | 22 | 315306.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_overcurrent
331 | Available | Input Register | U2 Frequency abnormal | Boolean | 15305 | 23 | 315306.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Frequency_abnormal
332 | Available | Input Register | U2 Temperature abnormal | Boolean | 15305 | 24 | 315306.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Temperature_abnormal
333 | Available | Input Register | U2 Hardware fault | Boolean | 15305 | 25 | 315306.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Hardware_fault
334 | Available | Input Register | U2 Grounding fault | Boolean | 15305 | 26 | 315306.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Grounding_fault
335 | Available | Input Register | U2 Bus overvoltage | Boolean | 15305 | 27 | 315306.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Bus_overvoltage
336 | Available | Input Register | U2 Bus undervoltage | Boolean | 15305 | 28 | 315306.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Bus_undervoltage
337 | Available | Input Register | U2 Inverter overvoltage | Boolean | 15305 | 29 | 315306.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Inverter_overvoltage
338 | Available | Input Register | U2 Fault State 2 | 32-bit bitfield | 15307 |  | 315308 |  |  |  |  | unitless | [9 empty] | IREG_15307_U2_Fault_State_2
339 | Available | Input Register | U2 Insulation impedance fault | Boolean | 15307 | 0 | 315308.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Insulation_impedance_fault
340 | Available | Input Register | U2 AC SPD fault | Boolean | 15307 | 1 | 315308.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_SPD_fault
341 | Available | Input Register | U2 Sampling fault | Boolean | 15307 | 2 | 315308.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Sampling_fault
342 | Available | Input Register | U2 DC polarity reversed alarm | Boolean | 15307 | 3 | 315308.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_polarity_reversed_alarm
343 | Available | Input Register | U2 Control power supply fault | Boolean | 15307 | 4 | 315308.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Control_power_supply_fault
344 | Available | Input Register | U2 Backup power supply fault | Boolean | 15307 | 5 | 315308.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Backup_power_supply_fault
345 | Available | Input Register | U2 AC current imballance | Boolean | 15307 | 6 | 315308.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_current_imballance
346 | Available | Input Register | U2 AC fuse fault | Boolean | 15307 | 7 | 315308.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_fuse_fault
347 | Available | Input Register | U2 DC SPD fault | Boolean | 15307 | 8 | 315308.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_SPD_fault
348 | Available | Input Register | U2 Buffer contactor fault | Boolean | 15307 | 9 | 315308.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Buffer_contactor_fault
349 | Available | Input Register | U2 DC injection fault | Boolean | 15307 | 10 | 315308.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_injection_fault
350 | Available | Input Register | U2 DC switch fault | Boolean | 15307 | 11 | 315308.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_switch_fault
351 | Available | Input Register | U2 Device code repeat fault | Boolean | 15307 | 12 | 315308.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Device_code_repeat_fault
352 | Available | Input Register | U2 Parallel operation communication failure | Boolean | 15307 | 13 | 315308.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Parallel_operation_communication_failure
353 | Available | Input Register | U2 Control cabinet temperature alarm | Boolean | 15307 | 14 | 315308.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Control_cabinet_temperature_alarm
354 | Available | Input Register | U2 DC fuse grounding fault | Boolean | 15307 | 15 | 315308.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_fuse_grounding_fault
355 | Available | Input Register | U2 Reversed branch over current | Boolean | 15307 | 16 | 315308.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Reversed_branch_over_current
356 | Available | Input Register | U2 Grid voltage imballance | Boolean | 15307 | 17 | 315308.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Grid_voltage_imballance
357 | Available | Input Register | U2 AC cabinet temperature alarm | Boolean | 15307 | 20 | 315308.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_cabinet_temperature_alarm
358 | Available | Input Register | U2 AC switch disconnection | Boolean | 15307 | 21 | 315308.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_switch_disconnection
359 | Available | Input Register | U2 AC switch fault | Boolean | 15307 | 22 | 315308.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_switch_fault
360 | Available | Input Register | U2 Soft start fault | Boolean | 15307 | 23 | 315308.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Soft_start_fault
361 | Available | Input Register | U2 DC voltage sampling fault | Boolean | 15307 | 24 | 315308.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_voltage_sampling_fault
362 | Available | Input Register | U2 Fan 2 fault | Boolean | 15307 | 25 | 315308.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Fan_2_fault
363 | Available | Input Register | U2 Current unbalance 2 | Boolean | 15307 | 26 | 315308.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Current_unbalance_2
364 | Available | Input Register | U2 Current unbalance 3 | Boolean | 15307 | 27 | 315308.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Current_unbalance_3
365 | Available | Input Register | U2 Drive board fault | Boolean | 15307 | 28 | 315308.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Drive_board_fault
366 | Available | Input Register | U2 DC cabinet temperature alarm | Boolean | 15307 | 29 | 315308.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_cabinet_temperature_alarm
367 | Available | Input Register | U2 Neutral point potential shift alarm | Boolean | 15307 | 30 | 315308.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Neutral_point_potential_shift_alarm
368 | Available | Input Register | U2 Carrier sync failure | Boolean | 15307 | 31 | 315308.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Carrier_sync_failure
369 | Available | Input Register | U2 Node State 1 | 32-bit bitfield | 15313 |  | 315314 |  |  |  |  | unitless | [9 empty] | IREG_15313_U2_Node_State_1
370 | Available | Input Register | U2 AC circuit breaker status | Boolean | 15313 | 0 | 315314.0 |  | None | Closed | Open | [10 empty] | IREG_15313_U2_AC_circuit_breaker_status
371 | Available | Input Register | U2 AC main contactor status | Boolean | 15313 | 1 | 315314.1 |  | None | Closed | Open | [10 empty] | IREG_15313_U2_AC_main_contactor_status
372 | Available | Input Register | U2 ABC fault | Boolean | 15313 | 12 | 315314.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15313_U2_ABC_fault
373 | Available | Input Register | U2 ABC local remote status | Boolean | 15313 | 13 | 315314.13 |  | Off (0) | Remote | Local | [10 empty] | IREG_15313_U2_ABC_local_remote_status
374 | Available | Input Register | U2 Node State 2 | 32-bit bitfield | 15315 |  | 315316 |  |  |  |  | unitless | [9 empty] | IREG_15315_U2_Node_State_2
375 | Available | Input Register | U2 SPD status | Boolean | 15315 | 12 | 315316.12 |  | None | Closed | Open | [10 empty] | IREG_15315_U2_SPD_status
376 | Available | Input Register | U2 DC switch 1 status | Boolean | 15315 | 20 | 315316.20 |  | None | Closed | Open | [10 empty] | IREG_15315_U2_DC_switch_1_status
377 | Available | Input Register | U2 DC switch 2 status | Boolean | 15315 | 21 | 315316.21 |  | None | Closed | Open | [10 empty] | IREG_15315_U2_DC_switch_2_status
378 | Available | Input Register | U2 DC switch 3 status | Boolean | 15315 | 22 | 315316.22 |  | None | Closed | Open | [10 empty] | IREG_15315_U2_DC_switch_3_status
379 | Available | Input Register | U2 DC switch 4 status | Boolean | 15315 | 23 | 315316.23 |  | None | Closed | Open | [10 empty] | IREG_15315_U2_DC_switch_4_status
380 | Available | Input Register | U2 Temperature 1 | 16-bit signed integer | 15317 |  | 315318 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15317_U2_Temperature_1_degC
381 | Available | Input Register | U2 Temperature 2 | 16-bit signed integer | 15318 |  | 315319 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15318_U2_Temperature_2_degC
382 | Available | Input Register | U2 Temperature 3 | 16-bit signed integer | 15319 |  | 315320 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15319_U2_Temperature_3_degC
383 | Available | Input Register | U2 Temperature 4 | 16-bit signed integer | 15320 |  | 315321 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15320_U2_Temperature_4_degC
384 | Available | Input Register | U2 Temperature 5 | 16-bit signed integer | 15321 |  | 315322 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15321_U2_Temperature_5_degC
385 | Available | Input Register | U2 Temperature 6 | 16-bit signed integer | 15322 |  | 315323 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15322_U2_Temperature_6_degC
386 | Available | Input Register | U2 Positive Resistance to Ground | 32-bit unsigned integer | 15323 |  | 315324 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15323_U2_Positive_Resistance_to_Ground_kOhm
387 | Available | Input Register | U2 Negative Resistance to Ground | 32-bit unsigned integer | 15325 |  | 315326 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15325_U2_Negative_Resistance_to_Ground_kOhm
388 | Available | Input Register | U2 Work State | 32-bit bitfield | 15327 |  | 315328 |  |  |  |  | unitless | [9 empty] | IREG_15327_U2_Work_State
389 | Available | Input Register | U2 Running | Boolean | 15327 | 0 | 315328.0 |  | None | Running | Not Running | [10 empty] | IREG_15327_U2_Running
390 | Available | Input Register | U2 Stopped | Boolean | 15327 | 1 | 315328.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15327_U2_Stopped
391 | Available | Input Register | U2 Initial Standby | Boolean | 15327 | 2 | 315328.2 |  | None | Standby | Not Standby | [10 empty] | IREG_15327_U2_Initial_Standby
392 | Available | Input Register | U2 Key Stop | Boolean | 15327 | 3 | 315328.3 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15327_U2_Key_Stop
393 | Available | Input Register | U2 Standby | Boolean | 15327 | 4 | 315328.4 |  | None | Standby | Not Standby | [10 empty] | IREG_15327_U2_Standby
394 | Available | Input Register | U2 Emergency Stop | Boolean | 15327 | 5 | 315328.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Emergency_Stop
395 | Available | Input Register | U2 Starting | Boolean | 15327 | 6 | 315328.6 |  | None | Starting | Not Starting | [10 empty] | IREG_15327_U2_Starting
396 | Available | Input Register | U2 Stopping | Boolean | 15327 | 7 | 315328.7 |  | None | Stopping | Not Stopping | [10 empty] | IREG_15327_U2_Stopping
397 | Available | Input Register | U2 Fault Stop | Boolean | 15327 | 9 | 315328.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Fault_Stop
398 | Available | Input Register | U2 Alarm running | Boolean | 15327 | 10 | 315328.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Alarm_running
399 | Available | Input Register | U2 Derating running | Boolean | 15327 | 11 | 315328.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Derating_running
400 | Available | Input Register | U2 IO-DSP communication failure | Boolean | 15327 | 13 | 315328.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_IO_DSP_communication_failure
401 | Available | Input Register | U2 Inverter is running | Boolean | 15327 | 17 | 315328.17 |  | None | Running | Not Running | [10 empty] | IREG_15327_U2_Inverter_is_running
402 | Available | Input Register | U2 Inverter is stopped | Boolean | 15327 | 18 | 315328.18 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15327_U2_Inverter_is_stopped
403 | Available | Input Register | U2 Anti-PID active | Boolean | 15327 | 19 | 315328.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Anti_PID_active
404 | Available | Input Register | U2 IO-MDC communication abnormal | Boolean | 15327 | 20 | 315328.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_IO_MDC_communication_abnormal
405 | Available | Input Register | U2 Alarm State | 32-bit bitfield | 15329 |  | 315330 |  |  |  |  | unitless | [9 empty] | IREG_15329_U2_Alarm_State
406 | Available | Input Register | U2 Temperature alarm | Boolean | 15329 | 0 | 315330.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Temperature_alarm
407 | Available | Input Register | U2 Low insulation resistance alarm | Boolean | 15329 | 1 | 315330.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Low_insulation_resistance_alarm
408 | Available | Input Register | U2 GFRT operation alarm | Boolean | 15329 | 2 | 315330.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_GFRT_operation_alarm
409 | Available | Input Register | U2 CT unbalance | Boolean | 15329 | 3 | 315330.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_CT_unbalance
410 | Available | Input Register | U2 DC fuse failure | Boolean | 15329 | 4 | 315330.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_fuse_failure
411 | Available | Input Register | U2 DSP-MDC communication failure | Boolean | 15329 | 5 | 315330.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DSP_MDC_communication_failure
412 | Available | Input Register | U2 DC sensor fault | Boolean | 15329 | 6 | 315330.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_sensor_fault
413 | Available | Input Register | U2 DC SPD fault | Boolean | 15329 | 7 | 315330.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_SPD_fault
414 | Available | Input Register | U2 AC SPD fault | Boolean | 15329 | 8 | 315330.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_AC_SPD_fault
415 | Available | Input Register | U2 Bypass circuit breaker fault | Boolean | 15329 | 9 | 315330.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Bypass_circuit_breaker_fault
416 | Available | Input Register | U2 Bypass fuse abnormal / branch fault | Boolean | 15329 | 10 | 315330.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Bypass_fuse_abnormal___branch_fault
417 | Available | Input Register | U2 Ground fuse fault | Boolean | 15329 | 11 | 315330.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Ground_fuse_fault
418 | Available | Input Register | U2 DC switch fault | Boolean | 15329 | 12 | 315330.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_switch_fault
419 | Available | Input Register | U2 Anti-PID power supply | Boolean | 15329 | 13 | 315330.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Anti_PID_power_supply
420 | Available | Input Register | U2 Fan fault | Boolean | 15329 | 14 | 315330.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Fan_fault
421 | Available | Input Register | U2 External power supply fault | Boolean | 15329 | 15 | 315330.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_External_power_supply_fault
422 | Available | Input Register | U2 DC bypass forward overcurrent alarm | Boolean | 15329 | 16 | 315330.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_bypass_forward_overcurrent_alarm
423 | Available | Input Register | U2 DC bypass reverse overcurrent alarm | Boolean | 15329 | 17 | 315330.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_bypass_reverse_overcurrent_alarm
424 | Available | Input Register | U2 Tributary board communication failure | Boolean | 15329 | 18 | 315330.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Tributary_board_communication_failure
425 | Available | Input Register | U2 AC circuit breaker fault | Boolean | 15329 | 19 | 315330.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_AC_circuit_breaker_fault
426 | Available | Input Register | U2 Meter communication failure | Boolean | 15329 | 20 | 315330.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Meter_communication_failure
427 | Available | Input Register | U2 Fan 2 fault | Boolean | 15329 | 21 | 315330.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Fan_2_fault
428 | Available | Input Register | U2 Contactor contact fault | Boolean | 15329 | 22 | 315330.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Contactor_contact_fault
429 | Available | Input Register | U2 Temperature and humidity sensor fault | Boolean | 15329 | 23 | 315330.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Temperature_and_humidity_sensor_fault
430 | Available | Input Register | U2 Frequency deviation active power regulation | Boolean | 15329 | 24 | 315330.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Frequency_deviation_active_power_regulation
431 | Available | Input Register | U2 Voltage deviation reactive power regulation | Boolean | 15329 | 25 | 315330.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Voltage_deviation_reactive_power_regulation
432 | Available | Input Register | U2 Insulation impedance sensor fault | Boolean | 15329 | 26 | 315330.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Insulation_impedance_sensor_fault
433 | Available | Input Register | U2 Busbar temperature alarm | Boolean | 15329 | 27 | 315330.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Busbar_temperature_alarm
434 | Available | Input Register | U2 Abnormal derating of fan | Boolean | 15329 | 28 | 315330.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Abnormal_derating_of_fan
435 | Available | Input Register | U2 Frequency abnormal | Boolean | 15329 | 30 | 315330.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Frequency_abnormal
436 | Available | Input Register | U2 Negative Voltage to Ground | 16-bit signed integer | 15331 |  | 315332 |  |  |  |  | V | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15331_U2_Negative_Voltage_to_Ground_V
437 | Available | Input Register | U2 Annual Power Yield | 32-bit unsigned integer | 15332 |  | 315333 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15332_U2_Annual_Power_Yield_kWh |  | This point is not mapped to ignition
438 | Available | Input Register | U2 CO2 Emission Reduction | 32-bit unsigned integer | 15334 |  | 315335 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15334_U2_CO2_Emission_Reduction_kg |  | This point is not mapped to ignition
439 | Available | Input Register | Certified Software Version | String | 15634 |  | 315635 | [14 empty] | IREG_15634_Certified_Software_Version |  | This point is not mapped to ignition
440 | Available | Input Register | Overexcitation Specified Active Power | 32-bit signed integer | 15699 |  | 315700 |  |  |  |  | kW | 10 | -2147483648 | 2147483647 | -214748364.8 | 214748364.7 |  |  |  |  | IREG_15699_Overexcitation_Specified_Active_Power_kW |  | This point is not mapped to ignition
441 | Available | Input Register | Underexcitation Specified Active Power | 32-bit signed integer | 15701 |  | 315702 |  |  |  |  | kW | 10 | -2147483648 | 2147483647 | -214748364.8 | 214748364.7 |  |  |  |  | IREG_15701_Underexcitation_Specified_Active_Power_kW |  | This point is not mapped to ignition
442 | Available | Input Register | Commercial Plant Running Status | 16-bit unsigned integer | 15703 |  | 315704 |  | Off (0) | Running | Offline | boolean |  | 0 | 65535 | [6 empty] | IREG_15703_Commercial_Plant_Running_Status_boolean |  | This point is not mapped to ignition
443 | Available | Input Register | Maximum Appearant Power | 16-bit unsigned integer | 15704 |  | 315705 |  |  |  |  | kVA | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15704_Maximum_Appearant_Power_kVA
444 | Available | Input Register | Maximum Discharging Power | 16-bit unsigned integer | 15705 |  | 315706 |  |  |  |  | kW | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15705_Maximum_Discharging_Power_kW |  | This point is not mapped to ignition
445 | Available | Input Register | Maximum inductive reactive power | 16-bit signed integer | 15706 |  | 315707 |  |  |  |  | kvar | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15706_Maximum_inductive_reactive_power_kvar
446 | Available | Input Register | Maximum capacitive reactive power | 16-bit signed integer | 15707 |  | 315708 |  |  |  |  | kvar | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15707_Maximum_capacitive_reactive_power_kvar
447 | Available | Input Register | Grid connected status of commercial plant | 16-bit unsigned integer | 15708 |  | 315709 |  | Off (0) | Connected | Disconnected | boolean |  | 0 | 65535 | [6 empty] | IREG_15708_Grid_connected_status_of_commercial_plant_boolean |  | This point is not mapped to ignition
448 | Available | Input Register | Nominal AC voltage | 16-bit unsigned integer | 15709 |  | 315710 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15709_Nominal_AC_voltage_V |  | This point is not mapped to ignition
449 | Available | Input Register | Max AC Voltage | 16-bit unsigned integer | 15710 |  | 315711 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15710_Max_AC_Voltage_V |  | This point is not mapped to ignition
450 | Available | Input Register | Min AC Voltage | 16-bit unsigned integer | 15711 |  | 315712 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15711_Min_AC_Voltage_V |  | This point is not mapped to ignition
451 | Available | Input Register | QU Reference Voltage Current Value | 16-bit unsigned integer | 15732 |  | 315733 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15732_QU_Reference_Voltage_Current_Value_V |  | This point is not mapped to ignition
452 | Available | Input Register | U1 Valid Recorder Quantity | 16-bit unsigned integer | 15733 |  | 315734 |  |  |  |  | count |  | 0 | 65535 | [6 empty] | IREG_15733_U1_Valid_Recorder_Quantity_count
453 | Available | Input Register | U2 Valid Recorder Quantity | 16-bit unsigned integer | 15734 |  | 315735 |  |  |  |  | count |  | 0 | 65535 | [6 empty] | IREG_15734_U2_Valid_Recorder_Quantity_count
454 | Available | Input Register | Zone Monitor Work State | Enumeration | 15999 |  | 316000 |  |  |  |  | unitless | [9 empty] | IREG_15999_Zone_Monitor_Work_State | 0 to 2
455 | Available | Input Register | Branch Open Circuit Alarm | 32-bit bitfield | 16000 |  | 316001 |  |  |  |  | unitless | [9 empty] | IREG_16000_Branch_Open_Circuit_Alarm
456 | Available | Input Register | U1 open circuit fault branch 1 | Boolean | 16000 | 0 | 316001.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_1
457 | Available | Input Register | U1 open circuit fault branch 2 | Boolean | 16000 | 1 | 316001.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_2
458 | Available | Input Register | U1 open circuit fault branch 3 | Boolean | 16000 | 2 | 316001.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_3
459 | Available | Input Register | U1 open circuit fault branch 4 | Boolean | 16000 | 3 | 316001.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_4
460 | Available | Input Register | U1 open circuit fault branch 5 | Boolean | 16000 | 4 | 316001.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_5
461 | Available | Input Register | U1 open circuit fault branch 6 | Boolean | 16000 | 5 | 316001.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_6
462 | Available | Input Register | U1 open circuit fault branch 7 | Boolean | 16000 | 6 | 316001.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_7
463 | Available | Input Register | U1 open circuit fault branch 8 | Boolean | 16000 | 7 | 316001.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_8
464 | Available | Input Register | U1 open circuit fault branch 9 | Boolean | 16000 | 8 | 316001.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_9
465 | Available | Input Register | U1 open circuit fault branch 10 | Boolean | 16000 | 9 | 316001.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_10
466 | Available | Input Register | U1 open circuit fault branch 11 | Boolean | 16000 | 10 | 316001.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_11
467 | Available | Input Register | U1 open circuit fault branch 12 | Boolean | 16000 | 11 | 316001.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_12
468 | Available | Input Register | U1 open circuit fault branch 13 | Boolean | 16000 | 12 | 316001.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_13
469 | Available | Input Register | U1 open circuit fault branch 14 | Boolean | 16000 | 13 | 316001.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_14
470 | Available | Input Register | U1 open circuit fault branch 15 | Boolean | 16000 | 14 | 316001.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_15
471 | Available | Input Register | U1 open circuit fault branch 16 | Boolean | 16000 | 15 | 316001.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_16
472 | Available | Input Register | U2 open circuit fault branch 1 | Boolean | 16000 | 16 | 316001.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_1
473 | Available | Input Register | U2 open circuit fault branch 2 | Boolean | 16000 | 17 | 316001.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_2
474 | Available | Input Register | U2 open circuit fault branch 3 | Boolean | 16000 | 18 | 316001.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_3
475 | Available | Input Register | U2 open circuit fault branch 4 | Boolean | 16000 | 19 | 316001.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_4
476 | Available | Input Register | U2 open circuit fault branch 5 | Boolean | 16000 | 20 | 316001.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_5
477 | Available | Input Register | U2 open circuit fault branch 6 | Boolean | 16000 | 21 | 316001.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_6
478 | Available | Input Register | U2 open circuit fault branch 7 | Boolean | 16000 | 22 | 316001.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_7
479 | Available | Input Register | U2 open circuit fault branch 8 | Boolean | 16000 | 23 | 316001.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_8
480 | Available | Input Register | U2 open circuit fault branch 9 | Boolean | 16000 | 24 | 316001.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_9
481 | Available | Input Register | U2 open circuit fault branch 10 | Boolean | 16000 | 25 | 316001.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_10
482 | Available | Input Register | U2 open circuit fault branch 11 | Boolean | 16000 | 26 | 316001.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_11
483 | Available | Input Register | U2 open circuit fault branch 12 | Boolean | 16000 | 27 | 316001.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_12
484 | Available | Input Register | U2 open circuit fault branch 13 | Boolean | 16000 | 28 | 316001.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_13
485 | Available | Input Register | U2 open circuit fault branch 14 | Boolean | 16000 | 29 | 316001.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_14
486 | Available | Input Register | U2 open circuit fault branch 15 | Boolean | 16000 | 30 | 316001.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_15
487 | Available | Input Register | U2 open circuit fault branch 16 | Boolean | 16000 | 31 | 316001.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_16
488 | Available | Input Register | Branch String Alarm | 32-bit bitfield | 16002 |  | 316003 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_Branch_String_Alarm
489 | Available | Input Register | U1 string failure branch 1 | Boolean | 16002 | 0 | 316003.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_1
490 | Available | Input Register | U1 string failure branch 2 | Boolean | 16002 | 1 | 316003.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_2
491 | Available | Input Register | U1 string failure branch 3 | Boolean | 16002 | 2 | 316003.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_3
492 | Available | Input Register | U1 string failure branch 4 | Boolean | 16002 | 3 | 316003.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_4
493 | Available | Input Register | U1 string failure branch 5 | Boolean | 16002 | 4 | 316003.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_5
494 | Available | Input Register | U1 string failure branch 6 | Boolean | 16002 | 5 | 316003.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_6
495 | Available | Input Register | U1 string failure branch 7 | Boolean | 16002 | 6 | 316003.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_7
496 | Available | Input Register | U1 string failure branch 8 | Boolean | 16002 | 7 | 316003.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_8
497 | Available | Input Register | U1 string failure branch 9 | Boolean | 16002 | 8 | 316003.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_9
498 | Available | Input Register | U1 string failure branch 10 | Boolean | 16002 | 9 | 316003.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_10
499 | Available | Input Register | U1 string failure branch 11 | Boolean | 16002 | 10 | 316003.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_11
500 | Available | Input Register | U1 string failure branch 12 | Boolean | 16002 | 11 | 316003.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_12
501 | Available | Input Register | U1 string failure branch 13 | Boolean | 16002 | 12 | 316003.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_13
502 | Available | Input Register | U1 string failure branch 14 | Boolean | 16002 | 13 | 316003.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_14
503 | Available | Input Register | U1 string failure branch 15 | Boolean | 16002 | 14 | 316003.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_15
504 | Available | Input Register | U1 string failure branch 16 | Boolean | 16002 | 15 | 316003.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_16
505 | Available | Input Register | U2 string failure branch 1 | Boolean | 16002 | 16 | 316003.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_1
506 | Available | Input Register | U2 string failure branch 2 | Boolean | 16002 | 17 | 316003.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_2
507 | Available | Input Register | U2 string failure branch 3 | Boolean | 16002 | 18 | 316003.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_3
508 | Available | Input Register | U2 string failure branch 4 | Boolean | 16002 | 19 | 316003.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_4
509 | Available | Input Register | U2 string failure branch 5 | Boolean | 16002 | 20 | 316003.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_5
510 | Available | Input Register | U2 string failure branch 6 | Boolean | 16002 | 21 | 316003.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_6
511 | Available | Input Register | U2 string failure branch 7 | Boolean | 16002 | 22 | 316003.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_7
512 | Available | Input Register | U2 string failure branch 8 | Boolean | 16002 | 23 | 316003.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_8
513 | Available | Input Register | U2 string failure branch 9 | Boolean | 16002 | 24 | 316003.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_9
514 | Available | Input Register | U2 string failure branch 10 | Boolean | 16002 | 25 | 316003.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_10
515 | Available | Input Register | U2 string failure branch 11 | Boolean | 16002 | 26 | 316003.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_11
516 | Available | Input Register | U2 string failure branch 12 | Boolean | 16002 | 27 | 316003.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_12
517 | Available | Input Register | U2 string failure branch 13 | Boolean | 16002 | 28 | 316003.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_13
518 | Available | Input Register | U2 string failure branch 14 | Boolean | 16002 | 29 | 316003.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_14
519 | Available | Input Register | U2 string failure branch 15 | Boolean | 16002 | 30 | 316003.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_15
520 | Available | Input Register | U2 string failure branch 16 | Boolean | 16002 | 31 | 316003.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_16
521 | Available | Input Register | U1 Warning Number of Strings Branch 1 | 16-bit unsigned integer | 16004 |  | 316005 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16004_U1_Warning_Number_of_Strings_Branch_1_count
522 | Available | Input Register | U1 Warning Number of Strings Branch 2 | 16-bit unsigned integer | 16005 |  | 316006 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16005_U1_Warning_Number_of_Strings_Branch_2_count
523 | Available | Input Register | U1 Warning Number of Strings Branch 3 | 16-bit unsigned integer | 16006 |  | 316007 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16006_U1_Warning_Number_of_Strings_Branch_3_count
524 | Available | Input Register | U1 Warning Number of Strings Branch 4 | 16-bit unsigned integer | 16007 |  | 316008 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16007_U1_Warning_Number_of_Strings_Branch_4_count
525 | Available | Input Register | U1 Warning Number of Strings Branch 5 | 16-bit unsigned integer | 16008 |  | 316009 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16008_U1_Warning_Number_of_Strings_Branch_5_count
526 | Available | Input Register | U1 Warning Number of Strings Branch 6 | 16-bit unsigned integer | 16009 |  | 316010 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16009_U1_Warning_Number_of_Strings_Branch_6_count
527 | Available | Input Register | U1 Warning Number of Strings Branch 7 | 16-bit unsigned integer | 16010 |  | 316011 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16010_U1_Warning_Number_of_Strings_Branch_7_count
528 | Available | Input Register | U1 Warning Number of Strings Branch 8 | 16-bit unsigned integer | 16011 |  | 316012 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16011_U1_Warning_Number_of_Strings_Branch_8_count
529 | Available | Input Register | U1 Warning Number of Strings Branch 9 | 16-bit unsigned integer | 16012 |  | 316013 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16012_U1_Warning_Number_of_Strings_Branch_9_count
530 | Available | Input Register | U1 Warning Number of Strings Branch 10 | 16-bit unsigned integer | 16013 |  | 316014 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16013_U1_Warning_Number_of_Strings_Branch_10_count
531 | Available | Input Register | U1 Warning Number of Strings Branch 11 | 16-bit unsigned integer | 16014 |  | 316015 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16014_U1_Warning_Number_of_Strings_Branch_11_count
532 | Available | Input Register | U1 Warning Number of Strings Branch 12 | 16-bit unsigned integer | 16015 |  | 316016 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16015_U1_Warning_Number_of_Strings_Branch_12_count
533 | Available | Input Register | U1 Warning Number of Strings Branch 13 | 16-bit unsigned integer | 16016 |  | 316017 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16016_U1_Warning_Number_of_Strings_Branch_13_count
534 | Available | Input Register | U1 Warning Number of Strings Branch 14 | 16-bit unsigned integer | 16017 |  | 316018 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16017_U1_Warning_Number_of_Strings_Branch_14_count
535 | Available | Input Register | U1 Warning Number of Strings Branch 15 | 16-bit unsigned integer | 16018 |  | 316019 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16018_U1_Warning_Number_of_Strings_Branch_15_count
536 | Available | Input Register | U1 Warning Number of Strings Branch 16 | 16-bit unsigned integer | 16019 |  | 316020 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16019_U1_Warning_Number_of_Strings_Branch_16_count
537 | Available | Input Register | U2 Warning Number of Strings Branch 1 | 16-bit unsigned integer | 16020 |  | 316021 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16020_U2_Warning_Number_of_Strings_Branch_1_count
538 | Available | Input Register | U2 Warning Number of Strings Branch 2 | 16-bit unsigned integer | 16021 |  | 316022 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16021_U2_Warning_Number_of_Strings_Branch_2_count
539 | Available | Input Register | U2 Warning Number of Strings Branch 3 | 16-bit unsigned integer | 16022 |  | 316023 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16022_U2_Warning_Number_of_Strings_Branch_3_count
540 | Available | Input Register | U2 Warning Number of Strings Branch 4 | 16-bit unsigned integer | 16023 |  | 316024 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16023_U2_Warning_Number_of_Strings_Branch_4_count
541 | Available | Input Register | U2 Warning Number of Strings Branch 5 | 16-bit unsigned integer | 16024 |  | 316025 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16024_U2_Warning_Number_of_Strings_Branch_5_count
542 | Available | Input Register | U2 Warning Number of Strings Branch 6 | 16-bit unsigned integer | 16025 |  | 316026 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16025_U2_Warning_Number_of_Strings_Branch_6_count
543 | Available | Input Register | U2 Warning Number of Strings Branch 7 | 16-bit unsigned integer | 16026 |  | 316027 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16026_U2_Warning_Number_of_Strings_Branch_7_count
544 | Available | Input Register | U2 Warning Number of Strings Branch 8 | 16-bit unsigned integer | 16027 |  | 316028 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16027_U2_Warning_Number_of_Strings_Branch_8_count
545 | Available | Input Register | U2 Warning Number of Strings Branch 9 | 16-bit unsigned integer | 16028 |  | 316029 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16028_U2_Warning_Number_of_Strings_Branch_9_count
546 | Available | Input Register | U2 Warning Number of Strings Branch 10 | 16-bit unsigned integer | 16029 |  | 316030 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16029_U2_Warning_Number_of_Strings_Branch_10_count
547 | Available | Input Register | U2 Warning Number of Strings Branch 11 | 16-bit unsigned integer | 16030 |  | 316031 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16030_U2_Warning_Number_of_Strings_Branch_11_count
548 | Available | Input Register | U2 Warning Number of Strings Branch 12 | 16-bit unsigned integer | 16031 |  | 316032 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16031_U2_Warning_Number_of_Strings_Branch_12_count
549 | Available | Input Register | U2 Warning Number of Strings Branch 13 | 16-bit unsigned integer | 16032 |  | 316033 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16032_U2_Warning_Number_of_Strings_Branch_13_count
550 | Available | Input Register | U2 Warning Number of Strings Branch 14 | 16-bit unsigned integer | 16033 |  | 316034 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16033_U2_Warning_Number_of_Strings_Branch_14_count
551 | Available | Input Register | U2 Warning Number of Strings Branch 15 | 16-bit unsigned integer | 16034 |  | 316035 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16034_U2_Warning_Number_of_Strings_Branch_15_count
552 | Available | Input Register | U2 Warning Number of Strings Branch 16 | 16-bit unsigned integer | 16035 |  | 316036 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16035_U2_Warning_Number_of_Strings_Branch_16_count
553 | Available | Holding Register | Set system clock year | 16-bit unsigned integer | 14999 |  | 415000 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_14999_Set_system_clock_year_year |  | This point is not mapped to ignition
554 | Available | Holding Register | Set system clock month | 16-bit unsigned integer | 15000 |  | 415001 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15000_Set_system_clock_month_month |  | This point is not mapped to ignition
555 | Available | Holding Register | Set system clock day | 16-bit unsigned integer | 15001 |  | 415002 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15001_Set_system_clock_day_day |  | This point is not mapped to ignition
556 | Available | Holding Register | Set system clock hour | 16-bit unsigned integer | 15002 |  | 415003 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15002_Set_system_clock_hour_hr |  | This point is not mapped to ignition
557 | Available | Holding Register | Set system clock minute | 16-bit unsigned integer | 15003 |  | 415004 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15003_Set_system_clock_minute_min |  | This point is not mapped to ignition
558 | Available | Holding Register | Set system clock second | 16-bit unsigned integer | 15004 |  | 415005 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15004_Set_system_clock_second_s |  | This point is not mapped to ignition
559 | Available | Holding Register | Start stop command | Enumeration | 15005 |  | 415006 |  |  |  |  | unitless | [9 empty] | HREG_15005_Start_stop_command | 16#CE to 16#CF
560 | Available | Holding Register | Emergency stop command | Enumeration | 15006 |  | 415007 |  |  |  |  | unitless | [9 empty] | HREG_15006_Emergency_stop_command | 16#CE to 16#CF
561 | Available | Holding Register | Active power percent | 16-bit unsigned integer | 15007 |  | 415008 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15007_Active_power_percent_pct |  | This point is not mapped to ignition
562 | Available | Holding Register | Local remote control | Enumeration | 15009 |  | 415010 |  |  |  |  | unitless | [9 empty] | HREG_15009_Local_remote_control | 1 to 3 | This point is not mapped to ignition
563 | Available | Holding Register | Reactive power mode | Enumeration | 15010 |  | 415011 |  |  |  |  | unitless | [9 empty] | HREG_15010_Reactive_power_mode | 16#55,16#A1 to 16#A5
564 | Available | Holding Register | Reactive power percent setpoint | 16-bit signed integer | 15011 |  | 415012 |  |  |  |  | % | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15011_Reactive_power_percent_setpoint_pct |  | This point is not mapped to ignition
565 | Available | Holding Register | Power factor setpoint | 16-bit signed integer | 15012 |  | 415013 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15012_Power_factor_setpoint_PU
566 | Available | Holding Register | Power limit actual value setpoint | 16-bit unsigned integer | 15013 |  | 415014 |  |  |  |  | kW | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15013_Power_limit_actual_value_setpoint_kW
567 | Available | Holding Register | Reactive power actual limit setpoint | 16-bit signed integer | 15014 |  | 415015 |  |  |  |  | kvar | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15014_Reactive_power_actual_limit_setpoint_kvar
568 | Available | Holding Register | Active power ramp up rate setpoint | 16-bit unsigned integer | 15015 |  | 415016 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15015_Active_power_ramp_up_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
569 | Available | Holding Register | Active power ramp down rate setpoint | 16-bit unsigned integer | 15016 |  | 415017 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15016_Active_power_ramp_down_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
570 | Available | Holding Register | Stop delay time | 16-bit unsigned integer | 15019 |  | 415020 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15019_Stop_delay_time_s |  | This point is not mapped to ignition
571 | Available | Holding Register | Stop slope | 16-bit unsigned integer | 15020 |  | 415021 |  |  |  |  | %/s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15020_Stop_slope_pct_per_s |  | This point is not mapped to ignition
572 | Available | Holding Register | High voltage load switch remote switch | 16-bit unsigned integer | 15025 |  | 415026 |  | On (1) | Local | Remote | boolean |  | 0 | 65535 | [6 empty] | HREG_15025_High_voltage_load_switch_remote_switch_boolean |  | This point is not mapped to ignition
573 | Available | Holding Register | Reactive power ramp up rate setpoint | 16-bit unsigned integer | 15026 |  | 415027 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15026_Reactive_power_ramp_up_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
574 | Available | Holding Register | Reactive power ramp down rate setpoint | 16-bit unsigned integer | 15027 |  | 415028 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15027_Reactive_power_ramp_down_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
575 | Available | Holding Register | Qu activation power point | 16-bit unsigned integer | 15028 |  | 415029 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15028_Qu_activation_power_point_pct |  | This point is not mapped to ignition
576 | Available | Holding Register | Qu operation mode | Enumeration | 15029 |  | 415030 |  |  |  |  | unitless | [9 empty] | HREG_15029_Qu_operation_mode | 16#A1 to 16#A3 | This point is not mapped to ignition
577 | Available | Holding Register | Qu input voltage source | Enumeration | 15030 |  | 415031 |  |  |  |  | unitless | [9 empty] | HREG_15030_Qu_input_voltage_source | 16#B1 to 16#B2 | This point is not mapped to ignition
578 | Available | Holding Register | Qu inductive reactive power limit setpoint | 16-bit unsigned integer | 15031 |  | 415032 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15031_Qu_inductive_reactive_power_limit_setpoint_pct |  | This point is not mapped to ignition
579 | Available | Holding Register | Qu capacitive reactive power limit setpoint | 16-bit unsigned integer | 15032 |  | 415033 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15032_Qu_capacitive_reactive_power_limit_setpoint_pct |  | This point is not mapped to ignition
580 | Available | Holding Register | Qu power factor end point | 16-bit unsigned integer | 15033 |  | 415034 |  |  |  |  | PU | 1000 | 0 | 65535 | 0 | 65.535 |  |  |  |  | HREG_15033_Qu_power_factor_end_point_PU |  | This point is not mapped to ignition
581 | Available | Holding Register | Qu power factor start point | 16-bit unsigned integer | 15034 |  | 415035 |  |  |  |  | PU | 1000 | 0 | 65535 | 0 | 65.535 |  |  |  |  | HREG_15034_Qu_power_factor_start_point_PU |  | This point is not mapped to ignition
582 | Available | Holding Register | Qu voltage rise start point | 16-bit unsigned integer | 15036 |  | 415037 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15036_Qu_voltage_rise_start_point_pct |  | This point is not mapped to ignition
583 | Available | Holding Register | Qu voltage rise end point | 16-bit unsigned integer | 15037 |  | 415038 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15037_Qu_voltage_rise_end_point_pct |  | This point is not mapped to ignition
584 | Available | Holding Register | Qu voltage drop start point | 16-bit unsigned integer | 15038 |  | 415039 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15038_Qu_voltage_drop_start_point_pct |  | This point is not mapped to ignition
585 | Available | Holding Register | Qu voltage drop end point | 16-bit unsigned integer | 15039 |  | 415040 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15039_Qu_voltage_drop_end_point_pct |  | This point is not mapped to ignition
586 | Available | Holding Register | Automatic voltage regulation benchmark | 16-bit unsigned integer | 15042 |  | 415043 |  |  |  |  | % | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15042_Automatic_voltage_regulation_benchmark_pct |  | This point is not mapped to ignition
587 | Available | Holding Register | Automatic voltage regulation hysterisis | 16-bit unsigned integer | 15043 |  | 415044 |  |  |  |  | % | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15043_Automatic_voltage_regulation_hysterisis_pct |  | This point is not mapped to ignition
588 | Available | Holding Register | Qu reactive power rising start | 16-bit signed integer | 15050 |  | 415051 |  |  |  |  | % | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15050_Qu_reactive_power_rising_start_pct |  | This point is not mapped to ignition
589 | Available | Holding Register | Qu reactive power decline start | 16-bit signed integer | 15051 |  | 415052 |  |  |  |  | % | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15051_Qu_reactive_power_decline_start_pct |  | This point is not mapped to ignition
590 | Available | Holding Register | Enable pu | Enumeration | 15054 |  | 415055 |  |  |  |  | unitless | [9 empty] | HREG_15054_Enable_pu | 16#55,16#AA | This point is not mapped to ignition
591 | Available | Holding Register | Pu active power rising gradiant | 16-bit unsigned integer | 15055 |  | 415056 |  |  |  |  | % | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15055_Pu_active_power_rising_gradiant_pct |  | This point is not mapped to ignition
592 | Available | Holding Register | Pu active power decline gradiant | 16-bit unsigned integer | 15056 |  | 415057 |  |  |  |  | % | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15056_Pu_active_power_decline_gradiant_pct |  | This point is not mapped to ignition
593 | Available | Holding Register | Dc switch open close | Enumeration | 15059 |  | 415060 |  |  |  |  | unitless | [9 empty] | HREG_15059_Dc_switch_open_close | 16#55,16#AA
594 | Available | Holding Register | Night svg enable disable | Enumeration | 15060 |  | 415061 |  |  |  |  | unitless | [9 empty] | HREG_15060_Night_svg_enable_disable | 16#55,16#AA | This point is not mapped to ignition
595 | Available | Holding Register | Start waiting time | 16-bit unsigned integer | 15061 |  | 415062 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15061_Start_waiting_time_s |  | This point is not mapped to ignition
596 | Available | Holding Register | Time for automatic recovery from fault | 16-bit unsigned integer | 15062 |  | 415063 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15062_Time_for_automatic_recovery_from_fault_s |  | This point is not mapped to ignition
597 | Available | Holding Register | Overfrequency recovery threshold | 16-bit unsigned integer | 15063 |  | 415064 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15063_Overfrequency_recovery_threshold_Hz |  | This point is not mapped to ignition
598 | Available | Holding Register | Underfrequency recovery threshold | 16-bit unsigned integer | 15064 |  | 415065 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15064_Underfrequency_recovery_threshold_Hz |  | This point is not mapped to ignition
599 | Available | Holding Register | Dc starting voltage | 16-bit unsigned integer | 15065 |  | 415066 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15065_Dc_starting_voltage_V |  | This point is not mapped to ignition
600 | Available | Holding Register | Overall mppt | Enumeration | 15068 |  | 415069 |  |  |  |  | unitless | [9 empty] | HREG_15068_Overall_mppt | 16#55,16#AA | This point is not mapped to ignition
601 | Available | Holding Register | Overall mppt calculation period | 16-bit unsigned integer | 15069 |  | 415070 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15069_Overall_mppt_calculation_period_min |  | This point is not mapped to ignition
602 | Available | Holding Register | Frequency modulation enable | Enumeration | 15072 |  | 415073 |  |  |  |  | unitless | [9 empty] | HREG_15072_Frequency_modulation_enable | 16#55,16#AA | This point is not mapped to ignition
603 | Available | Holding Register | Frequency regulation output change benchmark | Enumeration | 15073 |  | 415074 |  |  |  |  | unitless | [9 empty] | HREG_15073_Frequency_regulation_output_change_benchmark | 16#A1 to 16#A2 | This point is not mapped to ignition
604 | Available | Holding Register | Overfrequency derating start point | 16-bit unsigned integer | 15074 |  | 415075 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15074_Overfrequency_derating_start_point_Hz |  | This point is not mapped to ignition
605 | Available | Holding Register | Overfrequency derating end point | 16-bit unsigned integer | 15075 |  | 415076 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15075_Overfrequency_derating_end_point_Hz |  | This point is not mapped to ignition
606 | Available | Holding Register | Overfrequency derating factor | 16-bit unsigned integer | 15076 |  | 415077 |  |  |  |  | PU | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15076_Overfrequency_derating_factor_PU |  | This point is not mapped to ignition
607 | Available | Holding Register | Overfrequency derating limit | 16-bit unsigned integer | 15077 |  | 415078 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15077_Overfrequency_derating_limit_pct |  | This point is not mapped to ignition
608 | Available | Holding Register | Frequency regulation input source | Enumeration | 15078 |  | 415079 |  |  |  |  | unitless | [9 empty] | HREG_15078_Frequency_regulation_input_source | 16#B1 to 16#B2 | This point is not mapped to ignition
609 | Available | Holding Register | Frequency regulation active power | 16-bit unsigned integer | 15079 |  | 415080 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15079_Frequency_regulation_active_power_pct |  | This point is not mapped to ignition
610 | Available | Holding Register | Underfrequency rising start point | 16-bit unsigned integer | 15080 |  | 415081 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15080_Underfrequency_rising_start_point_Hz |  | This point is not mapped to ignition
611 | Available | Holding Register | Underfrequency rising end point | 16-bit unsigned integer | 15081 |  | 415082 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15081_Underfrequency_rising_end_point_Hz |  | This point is not mapped to ignition
612 | Available | Holding Register | Underfrequency rise factor | 16-bit unsigned integer | 15082 |  | 415083 |  |  |  |  | PU | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15082_Underfrequency_rise_factor_PU |  | This point is not mapped to ignition
613 | Available | Holding Register | Underfrequency rising limit | 16-bit unsigned integer | 15083 |  | 415084 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15083_Underfrequency_rising_limit_pct |  | This point is not mapped to ignition
614 | Available | Holding Register | Leakage current protection value | 16-bit unsigned integer | 15087 |  | 415088 |  |  |  |  | A | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15087_Leakage_current_protection_value_A |  | This point is not mapped to ignition
615 | Available | Holding Register | Ac overvoltage level 1 protection | 16-bit unsigned integer | 15119 |  | 415120 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15119_Ac_overvoltage_level_1_protection_pct |  | This point is not mapped to ignition
616 | Available | Holding Register | Ac overvoltage level 2 protection | 16-bit unsigned integer | 15120 |  | 415121 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15120_Ac_overvoltage_level_2_protection_pct |  | This point is not mapped to ignition
617 | Available | Holding Register | Ac overvoltage level 3 protection | 16-bit unsigned integer | 15121 |  | 415122 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15121_Ac_overvoltage_level_3_protection_pct |  | This point is not mapped to ignition
618 | Available | Holding Register | Ac overvoltage level 4 protection | 16-bit unsigned integer | 15122 |  | 415123 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15122_Ac_overvoltage_level_4_protection_pct |  | This point is not mapped to ignition
619 | Available | Holding Register | Ac overvoltage level 5 protection | 16-bit unsigned integer | 15123 |  | 415124 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15123_Ac_overvoltage_level_5_protection_pct |  | This point is not mapped to ignition
620 | Available | Holding Register | Vmax recover | 16-bit unsigned integer | 15129 |  | 415130 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15129_Vmax_recover_pct |  | This point is not mapped to ignition
621 | Available | Holding Register | Ac undervoltage level 1 protection | 16-bit unsigned integer | 15130 |  | 415131 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15130_Ac_undervoltage_level_1_protection_pct |  | This point is not mapped to ignition
622 | Available | Holding Register | Ac undervoltage level 2 protection | 16-bit unsigned integer | 15131 |  | 415132 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15131_Ac_undervoltage_level_2_protection_pct |  | This point is not mapped to ignition
623 | Available | Holding Register | Ac undervoltage level 3 protection | 16-bit unsigned integer | 15132 |  | 415133 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15132_Ac_undervoltage_level_3_protection_pct |  | This point is not mapped to ignition
624 | Available | Holding Register | Ac undervoltage level 4 protection | 16-bit unsigned integer | 15133 |  | 415134 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15133_Ac_undervoltage_level_4_protection_pct |  | This point is not mapped to ignition
625 | Available | Holding Register | Ac undervoltage level 5 protection | 16-bit unsigned integer | 15134 |  | 415135 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15134_Ac_undervoltage_level_5_protection_pct |  | This point is not mapped to ignition
626 | Available | Holding Register | Vmin recover | 16-bit unsigned integer | 15140 |  | 415141 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15140_Vmin_recover_pct |  | This point is not mapped to ignition
627 | Available | Holding Register | Grid over frequency level 1 protection | 16-bit unsigned integer | 15141 |  | 415142 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15141_Grid_over_frequency_level_1_protection_Hz |  | This point is not mapped to ignition
628 | Available | Holding Register | Grid over frequency level 2 protection | 16-bit unsigned integer | 15142 |  | 415143 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15142_Grid_over_frequency_level_2_protection_Hz |  | This point is not mapped to ignition
629 | Available | Holding Register | Grid over frequency level 3 protection | 16-bit unsigned integer | 15143 |  | 415144 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15143_Grid_over_frequency_level_3_protection_Hz |  | This point is not mapped to ignition
630 | Available | Holding Register | Grid over frequency level 4 protection | 16-bit unsigned integer | 15144 |  | 415145 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15144_Grid_over_frequency_level_4_protection_Hz |  | This point is not mapped to ignition
631 | Available | Holding Register | Grid over frequency level 5 protection | 16-bit unsigned integer | 15145 |  | 415146 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15145_Grid_over_frequency_level_5_protection_Hz |  | This point is not mapped to ignition
632 | Available | Holding Register | Fmax recover | 16-bit unsigned integer | 15151 |  | 415152 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15151_Fmax_recover_Hz |  | This point is not mapped to ignition
633 | Available | Holding Register | AC under frequency level 1 protection | 16-bit unsigned integer | 15152 |  | 415153 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15152_AC_under_frequency_level_1_protection_Hz |  | This point is not mapped to ignition
634 | Available | Holding Register | AC under frequency level 2 protection | 16-bit unsigned integer | 15153 |  | 415154 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15153_AC_under_frequency_level_2_protection_Hz |  | This point is not mapped to ignition
635 | Available | Holding Register | AC under frequency level 3 protection | 16-bit unsigned integer | 15154 |  | 415155 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15154_AC_under_frequency_level_3_protection_Hz |  | This point is not mapped to ignition
636 | Available | Holding Register | AC under frequency level 4 protection | 16-bit unsigned integer | 15155 |  | 415156 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15155_AC_under_frequency_level_4_protection_Hz |  | This point is not mapped to ignition
637 | Available | Holding Register | AC under frequency level 5 protection | 16-bit unsigned integer | 15156 |  | 415157 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15156_AC_under_frequency_level_5_protection_Hz |  | This point is not mapped to ignition
638 | Available | Holding Register | Fmin recover | 16-bit unsigned integer | 15162 |  | 415163 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15162_Fmin_recover_Hz |  | This point is not mapped to ignition
639 | Available | Holding Register | Floating mode | 16-bit unsigned integer | 15167 |  | 415168 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15167_Floating_mode_Hz |  | This point is not mapped to ignition
640 | Available | Holding Register | Over voltage level 1 trip time | 32-bit unsigned integer | 15169 |  | 415170 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15169_Over_voltage_level_1_trip_time_ms |  | This point is not mapped to ignition
641 | Available | Holding Register | Over voltage level 2 trip time | 16-bit unsigned integer | 15171 |  | 415172 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15171_Over_voltage_level_2_trip_time_ms |  | This point is not mapped to ignition
642 | Available | Holding Register | Over voltage level 3 trip time | 32-bit unsigned integer | 15173 |  | 415174 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15173_Over_voltage_level_3_trip_time_ms |  | This point is not mapped to ignition
643 | Available | Holding Register | Over voltage level 4 trip time | 16-bit unsigned integer | 15175 |  | 415176 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15175_Over_voltage_level_4_trip_time_ms |  | This point is not mapped to ignition
644 | Available | Holding Register | Over voltage level 5 trip time | 32-bit unsigned integer | 15177 |  | 415178 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15177_Over_voltage_level_5_trip_time_ms |  | This point is not mapped to ignition
645 | Available | Holding Register | Under voltage level 1 trip time | 16-bit unsigned integer | 15179 |  | 415180 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15179_Under_voltage_level_1_trip_time_ms |  | This point is not mapped to ignition
646 | Available | Holding Register | Under voltage level 2 trip time | 32-bit unsigned integer | 15181 |  | 415182 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15181_Under_voltage_level_2_trip_time_ms |  | This point is not mapped to ignition
647 | Available | Holding Register | Under voltage level 3 trip time | 16-bit unsigned integer | 15183 |  | 415184 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15183_Under_voltage_level_3_trip_time_ms |  | This point is not mapped to ignition
648 | Available | Holding Register | Under voltage level 4 trip time | 32-bit unsigned integer | 15185 |  | 415186 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15185_Under_voltage_level_4_trip_time_ms |  | This point is not mapped to ignition
649 | Available | Holding Register | Under voltage level 5 trip time | 16-bit unsigned integer | 15187 |  | 415188 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15187_Under_voltage_level_5_trip_time_ms |  | This point is not mapped to ignition
650 | Available | Holding Register | Over frequency level 1 trip time | 32-bit unsigned integer | 15189 |  | 415190 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15189_Over_frequency_level_1_trip_time_ms |  | This point is not mapped to ignition
651 | Available | Holding Register | Over frequency level 2 trip time | 32-bit unsigned integer | 15191 |  | 415192 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15191_Over_frequency_level_2_trip_time_ms |  | This point is not mapped to ignition
652 | Available | Holding Register | Over frequency level 3 trip time | 32-bit unsigned integer | 15193 |  | 415194 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15193_Over_frequency_level_3_trip_time_ms |  | This point is not mapped to ignition
653 | Available | Holding Register | Over frequency level 4 trip time | 32-bit unsigned integer | 15195 |  | 415196 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15195_Over_frequency_level_4_trip_time_ms |  | This point is not mapped to ignition
654 | Available | Holding Register | Over frequency level 5 trip time | 32-bit unsigned integer | 15197 |  | 415198 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15197_Over_frequency_level_5_trip_time_ms |  | This point is not mapped to ignition
655 | Available | Holding Register | Under frequency level 1 trip time | 32-bit unsigned integer | 15199 |  | 415200 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15199_Under_frequency_level_1_trip_time_ms |  | This point is not mapped to ignition
656 | Available | Holding Register | Under frequency level 2 trip time | 32-bit unsigned integer | 15201 |  | 415202 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15201_Under_frequency_level_2_trip_time_ms |  | This point is not mapped to ignition
657 | Available | Holding Register | Under frequency level 3 trip time | 32-bit unsigned integer | 15203 |  | 415204 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15203_Under_frequency_level_3_trip_time_ms |  | This point is not mapped to ignition
658 | Available | Holding Register | Under frequency level 4 trip time | 32-bit unsigned integer | 15205 |  | 415206 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15205_Under_frequency_level_4_trip_time_ms |  | This point is not mapped to ignition
659 | Available | Holding Register | Under frequency level 5 trip time | 32-bit unsigned integer | 15207 |  | 415208 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15207_Under_frequency_level_5_trip_time_ms |  | This point is not mapped to ignition
660 | Available | Holding Register | Active power control closed loop enable disable | Enumeration | 15211 |  | 415212 |  |  |  |  | unitless | [9 empty] | HREG_15211_Active_power_control_closed_loop_enable_disable | 16#55,16#AA | This point is not mapped to ignition
661 | Available | Holding Register | Reactive power control closed loop enable disable | Enumeration | 15212 |  | 415213 |  |  |  |  | unitless | [9 empty] | HREG_15212_Reactive_power_control_closed_loop_enable_disable | 16#55,16#AA | This point is not mapped to ignition
662 | Available | Holding Register | Reactive power response time | 16-bit unsigned integer | 15223 |  | 415224 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15223_Reactive_power_response_time_s |  | This point is not mapped to ignition
663 | Available | Holding Register | QP_K1 | 16-bit signed integer | 15224 |  | 415225 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15224_QP_K1_PU |  | This point is not mapped to ignition
664 | Available | Holding Register | QP_K2 | 16-bit signed integer | 15225 |  | 415226 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15225_QP_K2_PU |  | This point is not mapped to ignition
665 | Available | Holding Register | QP_K3 | 16-bit signed integer | 15226 |  | 415227 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15226_QP_K3_PU |  | This point is not mapped to ignition
666 | Available | Holding Register | QP_P1 | 16-bit unsigned integer | 15227 |  | 415228 |  |  |  |  | PU | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15227_QP_P1_PU |  | This point is not mapped to ignition
667 | Available | Holding Register | QP_P2 | 16-bit unsigned integer | 15228 |  | 415229 |  |  |  |  | PU | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15228_QP_P2_PU |  | This point is not mapped to ignition
668 | Available | Holding Register | QP_P3 | 16-bit unsigned integer | 15229 |  | 415230 |  |  |  |  | PU | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15229_QP_P3_PU |  | This point is not mapped to ignition
669 | Available | Holding Register | QP mode | Enumeration | 15230 |  | 415231 |  |  |  |  | unitless | [9 empty] | HREG_15230_QP_mode | 16#A1 to 16#A2 | This point is not mapped to ignition
670 | Available | Holding Register | Heartbeat | 16-bit unsigned integer | 15247 |  | 415248 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15247_Heartbeat_count |  | This point is not mapped to ignition
671 | Available | Holding Register | Heartbeat timeout period | 16-bit unsigned integer | 15248 |  | 415249 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15248_Heartbeat_timeout_period_s |  | This point is not mapped to ignition
672 | Available | Holding Register | Grid connection maximum voltage | 16-bit unsigned integer | 15256 |  | 415257 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15256_Grid_connection_maximum_voltage_pct |  | This point is not mapped to ignition
673 | Available | Holding Register | Grid connection minimum voltage | 16-bit unsigned integer | 15257 |  | 415258 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15257_Grid_connection_minimum_voltage_pct |  | This point is not mapped to ignition
674 | Available | Holding Register | Grid connection maximum frequency | 16-bit unsigned integer | 15258 |  | 415259 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15258_Grid_connection_maximum_frequency_Hz |  | This point is not mapped to ignition
675 | Available | Holding Register | Grid connection minimum frequency | 16-bit unsigned integer | 15259 |  | 415260 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15259_Grid_connection_minimum_frequency_Hz |  | This point is not mapped to ignition
676 | Available | Holding Register | Grid detection before connection | 16-bit unsigned integer | 15260 |  | 415261 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15260_Grid_detection_before_connection_s |  | This point is not mapped to ignition
677 | Available | Holding Register | Boot waiting time | 16-bit unsigned integer | 15261 |  | 415262 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15261_Boot_waiting_time_s |  | This point is not mapped to ignition
678 | Available | Holding Register | Specified overexcitation PF | 16-bit signed integer | 15264 |  | 415265 |  |  |  |  | PU | 0.001 | -32768 | 32767 | -32768000 | 32767000 |  |  |  |  | HREG_15264_Specified_overexcitation_PF_PU |  | This point is not mapped to ignition
679 | Available | Holding Register | Specified underrexcitation PF | 16-bit signed integer | 15265 |  | 415266 |  |  |  |  | PU | 0.001 | -32768 | 32767 | -32768000 | 32767000 |  |  |  |  | HREG_15265_Specified_underrexcitation_PF_PU |  | This point is not mapped to ignition
680 | Available | Holding Register | QU reference voltage automatic adjustment | 16-bit signed integer | 15266 |  | 415267 |  |  |  |  | unitless |  | -32768 | 32767 | [6 empty] | HREG_15266_QU_reference_voltage_automatic_adjustment | 16#55,16#AA | This point is not mapped to ignition
681 | Available | Holding Register | QU reference voltage adjustment | 16-bit unsigned integer | 15267 |  | 415268 |  |  |  |  | % | 0.1 | 0 | 65535 | 0 | 655350 |  |  |  |  | HREG_15267_QU_reference_voltage_adjustment_pct |  | This point is not mapped to ignition
682 | Available | Holding Register | QU reference voltage automatic adjustment time | 16-bit signed integer | 15268 |  | 415269 |  |  |  |  | s | 0.1 | -32768 | 32767 | -327680 | 327670 |  |  |  |  | HREG_15268_QU_reference_voltage_automatic_adjustment_time_s |  | This point is not mapped to ignition
683 | Available | Holding Register | Overvoltage derating start point | 16-bit unsigned integer | 15269 |  | 415270 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15269_Overvoltage_derating_start_point_pct |  | This point is not mapped to ignition
684 | Available | Holding Register | Overvoltage derating power start point | 16-bit unsigned integer | 15270 |  | 415271 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15270_Overvoltage_derating_power_start_point_pct |  | This point is not mapped to ignition
685 | Available | Holding Register | Overvoltage derating end point | 16-bit unsigned integer | 15271 |  | 415272 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15271_Overvoltage_derating_end_point_pct |  | This point is not mapped to ignition
686 | Available | Holding Register | Overvoltage derating power end point | 16-bit unsigned integer | 15272 |  | 415273 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15272_Overvoltage_derating_power_end_point_pct |  | This point is not mapped to ignition
687 | Available | Holding Register | Voltage derating response time | 16-bit unsigned integer | 15273 |  | 415274 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15273_Voltage_derating_response_time_s |  | This point is not mapped to ignition
688 | Available | Holding Register | Over frequency response time | 16-bit unsigned integer | 15274 |  | 415275 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15274_Over_frequency_response_time_s |  | This point is not mapped to ignition
689 | Available | Holding Register | Under frequency response time | 16-bit unsigned integer | 15275 |  | 415276 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15275_Under_frequency_response_time_s |  | This point is not mapped to ignition
690 | Available | Holding Register | Over frequency response delay time | 16-bit unsigned integer | 15280 |  | 415281 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15280_Over_frequency_response_delay_time_ms |  | This point is not mapped to ignition
691 | Available | Holding Register | Under frequency response delay time | 16-bit unsigned integer | 15281 |  | 415282 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15281_Under_frequency_response_delay_time_ms |  | This point is not mapped to ignition
692 | Available | Holding Register | Zone monitoring | 16-bit unsigned integer | 15799 |  | 415800 |  | State change | Enable | Disable | boolean |  | 0 | 65535 | [6 empty] | HREG_15799_Zone_monitoring_boolean |  | This point is not mapped to ignition
693 | Available | Holding Register | Sensitivity | 16-bit unsigned integer | 15801 |  | 415802 |  |  |  |  | unitless | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15801_Sensitivity |  | This point is not mapped to ignition
694 | Available | Holding Register | Clear zone monitor data | 16-bit unsigned integer | 15802 |  | 415803 |  | On (1) | Clear | No Action | boolean |  | 0 | 65535 | [6 empty] | HREG_15802_Clear_zone_monitor_data_boolean |  | This point is not mapped to ignition
695 | Available | Holding Register | Clear fault | 16-bit unsigned integer | 15803 |  | 415804 |  | On (1) | Clear | No Action | boolean |  | 0 | 65535 | [6 empty] | HREG_15803_Clear_fault_boolean |  | This point is not mapped to ignition
696 | Available | Holding Register | U1 number of strings on branch 1 | 16-bit unsigned integer | 15804 |  | 415805 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15804_U1_number_of_strings_on_branch_1_count |  | This point is not mapped to ignition
697 | Available | Holding Register | U1 number of strings on branch 2 | 16-bit unsigned integer | 15805 |  | 415806 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15805_U1_number_of_strings_on_branch_2_count |  | This point is not mapped to ignition
698 | Available | Holding Register | U1 number of strings on branch 3 | 16-bit unsigned integer | 15806 |  | 415807 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15806_U1_number_of_strings_on_branch_3_count |  | This point is not mapped to ignition
699 | Available | Holding Register | U1 number of strings on branch 4 | 16-bit unsigned integer | 15807 |  | 415808 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15807_U1_number_of_strings_on_branch_4_count |  | This point is not mapped to ignition
700 | Available | Holding Register | U1 number of strings on branch 5 | 16-bit unsigned integer | 15808 |  | 415809 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15808_U1_number_of_strings_on_branch_5_count |  | This point is not mapped to ignition
701 | Available | Holding Register | U1 number of strings on branch 6 | 16-bit unsigned integer | 15809 |  | 415810 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15809_U1_number_of_strings_on_branch_6_count |  | This point is not mapped to ignition
702 | Available | Holding Register | U1 number of strings on branch 7 | 16-bit unsigned integer | 15810 |  | 415811 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15810_U1_number_of_strings_on_branch_7_count |  | This point is not mapped to ignition
703 | Available | Holding Register | U1 number of strings on branch 8 | 16-bit unsigned integer | 15811 |  | 415812 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15811_U1_number_of_strings_on_branch_8_count |  | This point is not mapped to ignition
704 | Available | Holding Register | U1 number of strings on branch 9 | 16-bit unsigned integer | 15812 |  | 415813 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15812_U1_number_of_strings_on_branch_9_count |  | This point is not mapped to ignition
705 | Available | Holding Register | U1 number of strings on branch 10 | 16-bit unsigned integer | 15813 |  | 415814 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15813_U1_number_of_strings_on_branch_10_count |  | This point is not mapped to ignition
706 | Available | Holding Register | U1 number of strings on branch 11 | 16-bit unsigned integer | 15814 |  | 415815 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15814_U1_number_of_strings_on_branch_11_count |  | This point is not mapped to ignition
707 | Available | Holding Register | U1 number of strings on branch 12 | 16-bit unsigned integer | 15815 |  | 415816 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15815_U1_number_of_strings_on_branch_12_count |  | This point is not mapped to ignition
708 | Available | Holding Register | U1 number of strings on branch 13 | 16-bit unsigned integer | 15816 |  | 415817 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15816_U1_number_of_strings_on_branch_13_count |  | This point is not mapped to ignition
709 | Available | Holding Register | U1 number of strings on branch 14 | 16-bit unsigned integer | 15817 |  | 415818 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15817_U1_number_of_strings_on_branch_14_count |  | This point is not mapped to ignition
710 | Available | Holding Register | U1 number of strings on branch 15 | 16-bit unsigned integer | 15818 |  | 415819 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15818_U1_number_of_strings_on_branch_15_count |  | This point is not mapped to ignition
711 | Available | Holding Register | U1 number of strings on branch 16 | 16-bit unsigned integer | 15819 |  | 415820 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15819_U1_number_of_strings_on_branch_16_count |  | This point is not mapped to ignition
712 | Available | Holding Register | U2 number of strings on branch 1 | 16-bit unsigned integer | 15820 |  | 415821 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15820_U2_number_of_strings_on_branch_1_count |  | This point is not mapped to ignition
713 | Available | Holding Register | U2 number of strings on branch 2 | 16-bit unsigned integer | 15821 |  | 415822 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15821_U2_number_of_strings_on_branch_2_count |  | This point is not mapped to ignition
714 | Available | Holding Register | U2 number of strings on branch 3 | 16-bit unsigned integer | 15822 |  | 415823 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15822_U2_number_of_strings_on_branch_3_count |  | This point is not mapped to ignition
715 | Available | Holding Register | U2 number of strings on branch 4 | 16-bit unsigned integer | 15823 |  | 415824 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15823_U2_number_of_strings_on_branch_4_count |  | This point is not mapped to ignition
716 | Available | Holding Register | U2 number of strings on branch 5 | 16-bit unsigned integer | 15824 |  | 415825 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15824_U2_number_of_strings_on_branch_5_count |  | This point is not mapped to ignition
717 | Available | Holding Register | U2 number of strings on branch 6 | 16-bit unsigned integer | 15825 |  | 415826 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15825_U2_number_of_strings_on_branch_6_count |  | This point is not mapped to ignition
718 | Available | Holding Register | U2 number of strings on branch 7 | 16-bit unsigned integer | 15826 |  | 415827 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15826_U2_number_of_strings_on_branch_7_count |  | This point is not mapped to ignition
719 | Available | Holding Register | U2 number of strings on branch 8 | 16-bit unsigned integer | 15827 |  | 415828 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15827_U2_number_of_strings_on_branch_8_count |  | This point is not mapped to ignition
720 | Available | Holding Register | U2 number of strings on branch 9 | 16-bit unsigned integer | 15828 |  | 415829 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15828_U2_number_of_strings_on_branch_9_count |  | This point is not mapped to ignition
721 | Available | Holding Register | U2 number of strings on branch 10 | 16-bit unsigned integer | 15829 |  | 415830 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15829_U2_number_of_strings_on_branch_10_count |  | This point is not mapped to ignition
722 | Available | Holding Register | U2 number of strings on branch 11 | 16-bit unsigned integer | 15830 |  | 415831 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15830_U2_number_of_strings_on_branch_11_count |  | This point is not mapped to ignition
723 | Available | Holding Register | U2 number of strings on branch 12 | 16-bit unsigned integer | 15831 |  | 415832 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15831_U2_number_of_strings_on_branch_12_count |  | This point is not mapped to ignition
724 | Available | Holding Register | U2 number of strings on branch 13 | 16-bit unsigned integer | 15832 |  | 415833 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15832_U2_number_of_strings_on_branch_13_count |  | This point is not mapped to ignition
725 | Available | Holding Register | U2 number of strings on branch 14 | 16-bit unsigned integer | 15833 |  | 415834 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15833_U2_number_of_strings_on_branch_14_count |  | This point is not mapped to ignition
726 | Available | Holding Register | U2 number of strings on branch 15 | 16-bit unsigned integer | 15834 |  | 415835 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15834_U2_number_of_strings_on_branch_15_count |  | This point is not mapped to ignition
727 | Available | Holding Register | U2 number of strings on branch 16 | 16-bit unsigned integer | 15835 |  | 415836 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15835_U2_number_of_strings_on_branch_16_count |  | This point is not mapped to ignition
Note on S6: Format: (Low-Low,Low,High,High-High)
Note on X460: Zone Monitor Work State: 0: Disable 1: Self-Study 2: Fault Detection
Note on X565: Start Stop Enumeration: 16#CE - Stop 16#CF - Start All others no operation
Note on W566: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Double check the meaning of the enumeration I think it might be backwards Reply: Enum was wrong, and is now fixed
Note on X566: Start Stop Enumeration: 16#CF - Emergency Stop All others no operation
Note on X568: Matt Munin: 1 - Remote Only 2 - Local Only 3 - Remote and Local Control
Note on X569: Reactive Power Mode: 16#55 - OFF 16#A1 - Power factor mode 16#A2 - Reactive output mode 16#A3 - QU mode 16#A4 - Voltage mode 16#A5 - QP mode
Note on X582: QU Operation Mode: 16#A1 - Reactive power ratio mode 16#A2 - Active power ratio mode 16#A3 - Power factor mode
Note on X583: Voltage Source: 16#B1 - real time voltage 16#B2 - record voltage
Note on X596: Enable Disable P(U): 16#55 - Disable 16#AA - Enable
Note on X599: DC Switch Open/Close: 16#55 - Close 16#AA - Open
Note on X600: Night SVG Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X606: MPPT Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X608: Frequency modulation Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X609: Frequency output change benchmark: 16#A1 - function u nknown 16#A2 - function unknown
Note on X614: Frequency Source: 16#B1 - real time frequency 16#B2 - record frequency
Note on X666: Active Power Closed Loop Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X667: Reactive Power Closed Loop Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X675: Frequency output change benchmark: 16#A1 - function u nknown 16#A2 - function unknown
Note on X686: Reactive Power Closed Loop Enable/Disable: 16#55 - Disable 16#AA - Enable

## Inverters to PPC - SG4400UD
Site Name | [5 empty] | Modbus |  |  |  | Inverters to PPC-1
Last updated |  | 2024-04-01 | Device Type | Sungrow SG4400UD | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 5 | Subsystem / Zone | Inverters
Device Register Base |  | 1 | [7 empty] | CAUTION: Sungrow device uses multiple endian conventions on a per-register basis. Consult sungrow manual for endian convention rubric.
Register Digits |  | 6
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Not Imported | Input Register | Protocol Number | 32-bit unsigned integer | 14999 |  | 315000 |  |  |  |  | unitless |  | 0 | 4294967295 | [6 empty] | IREG_14999_Protocol_Number |  | This point is not mapped to ignition
2 | Not Imported | Input Register | Protocol Version | 32-bit unsigned integer | 15001 |  | 315002 |  |  |  |  | unitless |  | 0 | 4294967295 | [6 empty] | IREG_15001_Protocol_Version |  | This point is not mapped to ignition
3 | Not Imported | Input Register | Serial Number | String | 15003 |  | 315004 | [14 empty] | IREG_15003_Serial_Number |  | This point is not mapped to ignition
4 | Not Imported | Input Register | Machine Model | String | 15011 |  | 315012 | [14 empty] | IREG_15011_Machine_Model |  | This point is not mapped to ignition
5 | Available | Input Register | Device Type Code | 16-bit unsigned integer | 15069 |  | 315070 |  |  |  |  | unitless | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15069_Device_Type_Code |  | This point is not mapped to ignition
6 | Available | Input Register | Rated active power | 16-bit unsigned integer | 15070 |  | 315071 |  |  |  |  | kW | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15070_Rated_active_power_kW |  | This point is not mapped to ignition
7 | Available | Input Register | Daily Power yield | 32-bit unsigned integer | 15072 |  | 315073 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15072_Daily_Power_yield_kWh
8 | Available | Input Register | Monthly Power yield | 32-bit unsigned integer | 15074 |  | 315075 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15074_Monthly_Power_yield_kWh |  | This point is not mapped to ignition
9 | Available | Input Register | Total Power yield | 32-bit unsigned integer | 15076 |  | 315077 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15076_Total_Power_yield_kWh
10 | Available | Input Register | CO2 emission reduction | 32-bit unsigned integer | 15078 |  | 315079 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15078_CO2_emission_reduction_kg |  | This point is not mapped to ignition
11 | Available | Input Register | Daily grid connected minutes | 16-bit unsigned integer | 15080 |  | 315081 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15080_Daily_grid_connected_minutes_min |  | This point is not mapped to ignition
12 | Available | Input Register | Total Running Hours | 32-bit unsigned integer | 15081 |  | 315082 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15081_Total_Running_Hours_hr
13 | Available | Input Register | Total DC Power | 32-bit signed integer | 15091 |  | 315092 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15091_Total_DC_Power_W
14 | Available | Input Register | A-B Line Voltage | 16-bit unsigned integer | 15093 |  | 315094 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15093_A_B_Line_Voltage_V
15 | Available | Input Register | B-C Line Voltage | 16-bit unsigned integer | 15094 |  | 315095 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15094_B_C_Line_Voltage_V
16 | Available | Input Register | C-A Line Voltage | 16-bit unsigned integer | 15095 |  | 315096 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15095_C_A_Line_Voltage_V
17 | Available | Input Register | Phase A Current | 16-bit unsigned integer | 15096 |  | 315097 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15096_Phase_A_Current_A
18 | Available | Input Register | Phase B Current | 16-bit unsigned integer | 15097 |  | 315098 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15097_Phase_B_Current_A
19 | Available | Input Register | Phase C Current | 16-bit unsigned integer | 15098 |  | 315099 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15098_Phase_C_Current_A
20 | Available | Input Register | Total active power | 32-bit signed integer | 15099 |  | 315100 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15099_Total_active_power_W
21 | Available | Input Register | Total reactive power | 32-bit signed integer | 15101 |  | 315102 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15101_Total_reactive_power_var
22 | Available | Input Register | Total appearant power | 32-bit unsigned integer | 15103 |  | 315104 |  |  |  |  | VA | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15103_Total_appearant_power_VA |  | This point is not mapped to ignition
23 | Available | Input Register | Power Factor | 16-bit signed integer | 15105 |  | 315106 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15105_Power_Factor_PU
24 | Available | Input Register | Frequency | 16-bit unsigned integer | 15106 |  | 315107 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15106_Frequency_Hz
25 | Not Imported | Input Register | Rated reactive power | 16-bit unsigned integer | 15107 |  | 315108 |  |  |  |  | kvar | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15107_Rated_reactive_power_kvar |  | This point is not mapped to ignition
26 | Available | Input Register | Power limit actual value feedback | 32-bit unsigned integer | 15108 |  | 315109 |  |  |  |  | W | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15108_Power_limit_actual_value_feedback_W
27 | Available | Input Register | Reactive power adjustment actual value feedback | 32-bit signed integer | 15110 |  | 315111 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15110_Reactive_power_adjustment_actual_value_feedback_var
28 | Available | Input Register | Power factor feedback | 16-bit signed integer | 15112 |  | 315113 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15112_Power_factor_feedback_PU
29 | Available | Input Register | Transformer node state | 16-bit bitfield | 15113 |  | 315114 | [14 empty] | IREG_15113_Transformer_node_state
30 | Available | Input Register | Transformer gas buildup trip | Boolean | 15113 | 0 | 315114.0 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_gas_buildup_trip
31 | Available | Input Register | Transformer gas buildup alarm | Boolean | 15113 | 1 | 315114.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_gas_buildup_alarm
32 | Available | Input Register | Transformer oil temperature alarm | Boolean | 15113 | 2 | 315114.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_oil_temperature_alarm
33 | Available | Input Register | Transformer oil temperature trip | Boolean | 15113 | 3 | 315114.3 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_oil_temperature_trip
34 | Available | Input Register | Transformer low oil level trip | Boolean | 15113 | 4 | 315114.4 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_low_oil_level_trip
35 | Available | Input Register | Transformer low oil level alarm | Boolean | 15113 | 5 | 315114.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_low_oil_level_alarm
36 | Available | Input Register | Transformer pressure relief valve trip | Boolean | 15113 | 6 | 315114.6 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_pressure_relief_valve_trip
37 | Available | Input Register | MV load switch 1 status | Boolean | 15113 | 8 | 315114.8 |  | None | Closed | Open | [10 empty] | IREG_15113_MV__load_switch_1_status
38 | Available | Input Register | MV load switch 2 status | Boolean | 15113 | 9 | 315114.9 |  | None | Closed | Open | [10 empty] | IREG_15113_MV__load_switch_2_status
39 | Available | Input Register | Disconnector status | Boolean | 15113 | 11 | 315114.11 |  | None | Closed | Open | [10 empty] | IREG_15113_Disconnector_status
40 | Available | Input Register | Transformer high oil level alarm | Boolean | 15113 | 13 | 315114.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_high_oil_level_alarm
41 | Available | Input Register | Transformer winding temperature trip | Boolean | 15113 | 14 | 315114.14 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15113_Transformer_winding_temperature_trip
42 | Available | Input Register | Transformer winding temperature alarm | Boolean | 15113 | 15 | 315114.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15113_Transformer_winding_temperature_alarm
43 | Available | Input Register | Annual power yields | 32-bit unsigned integer | 15114 |  | 315115 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15114_Annual_power_yields_kWh |  | This point is not mapped to ignition
44 | Available | Input Register | Overall work state | 32-bit bitfield | 15116 |  | 315117 | [14 empty] | IREG_15116_Overall_work_state
45 | Available | Input Register | Running | Boolean | 15116 | 0 | 315117.0 |  | None | Running | Not Running | [10 empty] | IREG_15116_Running
46 | Available | Input Register | Stopped | Boolean | 15116 | 1 | 315117.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15116_Stopped
47 | Available | Input Register | Remote emergency stop | Boolean | 15116 | 3 | 315117.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_Remote_emergency_stop
48 | Available | Input Register | Local emergency stop | Boolean | 15116 | 6 | 315117.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15116_Local_emergency_stop
49 | Available | Input Register | SCU master fault | Boolean | 15116 | 7 | 315117.7 |  | On (1) | Faulted | Normal | [10 empty] | IREG_15116_SCU_master_fault
50 | Available | Input Register | Running | Boolean | 15116 | 8 | 315117.8 |  | None | Running | Not Running | [10 empty] | IREG_15116_Running
51 | Available | Input Register | Warn run | Boolean | 15116 | 9 | 315117.9 |  | None | Alarm Running | Not Running | [10 empty] | IREG_15116_Warn_run
52 | Available | Input Register | Faulted | Boolean | 15116 | 10 | 315117.10 |  | None | Faulted | Not Faulted | [10 empty] | IREG_15116_Faulted
53 | Available | Input Register | Stopped | Boolean | 15116 | 11 | 315117.11 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15116_Stopped
54 | Available | Input Register | AC insulation fault | Boolean | 15116 | 12 | 315117.12 |  | On (1) | Faulted | Normal | [10 empty] | IREG_15116_AC_insulation_fault
55 | Available | Input Register | SCU slave fault | Boolean | 15116 | 13 | 315117.13 |  | On (1) | Faulted | Normal | [10 empty] | IREG_15116_SCU_slave_fault
56 | Available | Input Register | 24h insulation fault | Boolean | 15116 | 15 | 315117.15 |  | On (1) | Faulted | Normal | [10 empty] | IREG_15116_24h_insulation_fault
57 | Available | Input Register | 24h DC insulation fault | Boolean | 15116 | 16 | 315117.16 |  | On (1) | Faulted | Normal | [10 empty] | IREG_15116_24h_DC_insulation_fault
58 | Available | Input Register | 24h AC insulation fault | Boolean | 15116 | 17 | 315117.17 |  | On (1) | Faulted | Normal | [10 empty] | IREG_15116_24h_AC_insulation_fault
59 | Available | Input Register | Transformer oil temperature | 16-bit signed integer | 15118 |  | 315119 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15118_Transformer_oil_temperature_degC
60 | Available | Input Register | Winding temperature | 16-bit signed integer | 15119 |  | 315120 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15119_Winding_temperature_degC
61 | Available | Input Register | MV Node State 1 | 16-bit bitfield | 15125 |  | 315126 | [14 empty] | IREG_15125_MV_Node_State_1
62 | Available | Input Register | External emergency stop mv node state | Boolean | 15125 | 11 | 315126.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_External_emergency_stop_mv_node_state
63 | Available | Input Register | MV fuse blown alarm | Boolean | 15125 | 12 | 315126.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_MV_fuse_blown_alarm
64 | Available | Input Register | HV compartment smoke alarm | Boolean | 15125 | 13 | 315126.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15125_HV_compartment_smoke_alarm
65 | Available | Input Register | HV Local remote switch status | Boolean | 15125 | 14 | 315126.14 |  | On (1) | Local | Remote | [10 empty] | IREG_15125_HV_Local_remote_switch_status
66 | Available | Input Register | Overall alarm state | 16-bit bitfield | 15126 |  | 315127 | [14 empty] | IREG_15126_Overall_alarm_state
67 | Available | Input Register | MV fan status | Boolean | 15126 | 1 | 315127.1 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_MV_fan_status
68 | Available | Input Register | AC insulation detection communication status | Boolean | 15126 | 4 | 315127.4 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_AC_insulation_detection_communication_status
69 | Available | Input Register | 24h insulation alarm | Boolean | 15126 | 6 | 315127.6 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_24h_insulation_alarm
70 | Available | Input Register | SCU master-slave communication status | Boolean | 15126 | 7 | 315127.7 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_SCU_master_slave_communication_status
71 | Available | Input Register | Heartbeat status | Boolean | 15126 | 8 | 315127.8 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_Heartbeat_status
72 | Available | Input Register | PMD IO board communication status | Boolean | 15126 | 9 | 315127.9 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_PMD_IO_board_communication_status
73 | Available | Input Register | Inverter IO board communication status | Boolean | 15126 | 11 | 315127.11 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_Inverter_IO_board_communication_status
74 | Available | Input Register | ISO board communication status | Boolean | 15126 | 14 | 315127.14 |  |  | Abnormal | Normal | [10 empty] | IREG_15126_ISO_board_communication_status
75 | Available | Input Register | Digital input state | 32-bit bitfield | 15128 |  | 315129 | [14 empty] | IREG_15128_Digital_input_state
76 | Available | Input Register | DI1 status | Boolean | 15128 | 0 | 315129.0 |  | None | Closed | Open | [10 empty] | IREG_15128_DI1_status
77 | Available | Input Register | DI2 status | Boolean | 15128 | 1 | 315129.1 |  | None | Closed | Open | [10 empty] | IREG_15128_DI2_status
78 | Available | Input Register | DI3 status | Boolean | 15128 | 2 | 315129.2 |  | None | Closed | Closed | [10 empty] | IREG_15128_DI3_status
79 | Available | Input Register | DI4 status | Boolean | 15128 | 3 | 315129.3 |  | None | Closed | Closed | [10 empty] | IREG_15128_DI4_status
80 | Available | Input Register | DI5 status | Boolean | 15128 | 4 | 315129.4 |  | None | Closed | Closed | [10 empty] | IREG_15128_DI5_status
81 | Available | Input Register | DI6 status | Boolean | 15128 | 5 | 315129.5 |  | None | Closed | Open | [10 empty] | IREG_15128_DI6_status
82 | Available | Input Register | DI7 status | Boolean | 15128 | 6 | 315129.6 |  | None | Closed | Open | [10 empty] | IREG_15128_DI7_status
83 | Available | Input Register | DI8 status | Boolean | 15128 | 7 | 315129.7 |  | None | Closed | Open | [10 empty] | IREG_15128_DI8_status
84 | Available | Input Register | DI9 status | Boolean | 15128 | 8 | 315129.8 |  | None | Closed | Open | [10 empty] | IREG_15128_DI9_status
85 | Available | Input Register | DI10 status | Boolean | 15128 | 9 | 315129.9 |  | None | Closed | Open | [10 empty] | IREG_15128_DI10_status
86 | Available | Input Register | DI11 status | Boolean | 15128 | 10 | 315129.10 |  | None | Closed | Open | [10 empty] | IREG_15128_DI11_status
87 | Available | Input Register | DI12 status | Boolean | 15128 | 11 | 315129.11 |  | None | Closed | Open | [10 empty] | IREG_15128_DI12_status
88 | Available | Input Register | DI13 status | Boolean | 15128 | 12 | 315129.12 |  | None | Closed | Open | [10 empty] | IREG_15128_DI13_status
89 | Available | Input Register | DI14 status | Boolean | 15128 | 13 | 315129.13 |  | None | Closed | Open | [10 empty] | IREG_15128_DI14_status
90 | Available | Input Register | DI15 status | Boolean | 15128 | 14 | 315129.14 |  | None | Closed | Open | [10 empty] | IREG_15128_DI15_status
91 | Available | Input Register | DI16 status | Boolean | 15128 | 15 | 315129.15 |  | None | Closed | Open | [10 empty] | IREG_15128_DI16_status
92 | Available | Input Register | DI17 status | Boolean | 15128 | 16 | 315129.16 |  | None | Closed | Open | [10 empty] | IREG_15128_DI17_status
93 | Available | Input Register | DI18 status | Boolean | 15128 | 17 | 315129.17 |  | None | Closed | Open | [10 empty] | IREG_15128_DI18_status
94 | Available | Input Register | DI19 status | Boolean | 15128 | 18 | 315129.18 |  | None | Closed | Open | [10 empty] | IREG_15128_DI19_status
95 | Available | Input Register | DI20 status | Boolean | 15128 | 19 | 315129.19 |  | None | Closed | Open | [10 empty] | IREG_15128_DI20_status
96 | Available | Input Register | DI21 status | Boolean | 15128 | 20 | 315129.20 |  | None | Closed | Open | [10 empty] | IREG_15128_DI21_status
97 | Available | Input Register | DI22 status | Boolean | 15128 | 21 | 315129.21 |  | None | Closed | Open | [10 empty] | IREG_15128_DI22_status
98 | Available | Input Register | DI23 status | Boolean | 15128 | 22 | 315129.22 |  | None | Closed | Open | [10 empty] | IREG_15128_DI23_status
99 | Available | Input Register | DI24 status | Boolean | 15128 | 23 | 315129.23 |  | None | Closed | Open | [10 empty] | IREG_15128_DI24_status
100 | Available | Input Register | MV Node state 2 | 32-bit bitfield | 15130 |  | 315131 | [14 empty] | IREG_15130_MV_Node_state_2
101 | Available | Input Register | MV load switch status | Boolean | 15130 | 0 | 315131.0 |  | None | Closed | Open | [10 empty] | IREG_15130_MV_load_switch_status
102 | Available | Input Register | HV remote trip | Boolean | 15130 | 1 | 315131.1 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15130_HV_remote_trip
103 | Available | Input Register | HV remote closing | Boolean | 15130 | 6 | 315131.6 |  | On (1) | Closed | Open | [10 empty] | IREG_15130_HV_remote_closing
104 | Available | Input Register | Transformer compartment door | Boolean | 15130 | 7 | 315131.7 |  | On (1) | Open | Closed | [10 empty] | IREG_15130_Transformer_compartment_door
105 | Available | Input Register | Transformer compartment smoke alarm | Boolean | 15130 | 8 | 315131.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15130_Transformer_compartment_smoke_alarm
106 | Available | Input Register | UPS fault | Boolean | 15130 | 9 | 315131.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15130_UPS_fault
107 | Available | Input Register | MV earthing switch status | Boolean | 15130 | 11 | 315131.11 |  | None | Closed | Open | [10 empty] | IREG_15130_MV_earthing_switch_status
108 | Available | Input Register | MV earthing switch 1 status | Boolean | 15130 | 12 | 315131.12 |  | None | Closed | Open | [10 empty] | IREG_15130_MV_earthing_switch_1_status
109 | Available | Input Register | MV earthing switch 2 status | Boolean | 15130 | 13 | 315131.13 |  | None | Closed | Open | [10 empty] | IREG_15130_MV_earthing_switch_2_status
110 | Available | Input Register | MV earthing switch 3 status | Boolean | 15130 | 14 | 315131.14 |  | None | Closed | Open | [10 empty] | IREG_15130_MV_earthing_switch_3_status
111 | Available | Input Register | High level trip | Boolean | 15130 | 15 | 315131.15 |  | On (1) | Tripped | Normal | [10 empty] | IREG_15130_High_level_trip
112 | Available | Input Register | Load switch T-A status | Boolean | 15130 | 18 | 315131.18 |  | None | Closed | Open | [10 empty] | IREG_15130_Load_switch_T_A_status
113 | Available | Input Register | Load switch T-B status | Boolean | 15130 | 19 | 315131.19 |  | None | Closed | Open | [10 empty] | IREG_15130_Load_switch_T_B_status
114 | Available | Input Register | Load switch T-AB status | Boolean | 15130 | 20 | 315131.20 |  | None | Closed | Open | [10 empty] | IREG_15130_Load_switch_T_AB_status
115 | Available | Input Register | Load switch A-B status | Boolean | 15130 | 21 | 315131.21 |  | None | Closed | Open | [10 empty] | IREG_15130_Load_switch_A_B_status
116 | Available | Input Register | PMD_IODI input status | 16-bit bitfield | 15141 |  | 315142 | [14 empty] | IREG_15141_PMD_IODI_input_status
117 | Available | Input Register | DI1 | Boolean | 15141 | 0 | 315142.0 |  | None | Closed | Open | [10 empty] | IREG_15141_DI1
118 | Available | Input Register | DI2 | Boolean | 15141 | 1 | 315142.1 |  | None | Closed | Open | [10 empty] | IREG_15141_DI2
119 | Available | Input Register | DI3 | Boolean | 15141 | 2 | 315142.2 |  | None | Closed | Open | [10 empty] | IREG_15141_DI3
120 | Available | Input Register | DI4 | Boolean | 15141 | 3 | 315142.3 |  | None | Closed | Open | [10 empty] | IREG_15141_DI4
121 | Available | Input Register | DI5 | Boolean | 15141 | 4 | 315142.4 |  | None | Closed | Open | [10 empty] | IREG_15141_DI5
122 | Available | Input Register | DI6 | Boolean | 15141 | 5 | 315142.5 |  | None | Closed | Open | [10 empty] | IREG_15141_DI6
123 | Available | Input Register | DI7 | Boolean | 15141 | 6 | 315142.6 |  | None | Closed | Open | [10 empty] | IREG_15141_DI7
124 | Available | Input Register | DI8 | Boolean | 15141 | 7 | 315142.7 |  | None | Closed | Open | [10 empty] | IREG_15141_DI8
125 | Available | Input Register | DI9 | Boolean | 15141 | 8 | 315142.8 |  | None | Closed | Open | [10 empty] | IREG_15141_DI9
126 | Available | Input Register | DI10 | Boolean | 15141 | 9 | 315142.9 |  | None | Closed | Open | [10 empty] | IREG_15141_DI10
127 | Available | Input Register | DI11 | Boolean | 15141 | 10 | 315142.10 |  | None | Closed | Open | [10 empty] | IREG_15141_DI11
128 | Available | Input Register | DI12 | Boolean | 15141 | 11 | 315142.11 |  | None | Closed | Open | [10 empty] | IREG_15141_DI12
129 | Available | Input Register | UPS conversion status | 16-bit bitfield | 15145 |  | 315146 | [14 empty] | IREG_15145_UPS_conversion_status
130 | Available | Input Register | UPS conversion | Boolean | 15145 | 0 | 315146.0 |  | None | Conversion | No Conversion | [10 empty] | IREG_15145_UPS_conversion__
131 | Available | Input Register | UPS alarm status | 16-bit bitfield | 15146 |  | 315147 | [14 empty] | IREG_15146_UPS_alarm_status
132 | Available | Input Register | UPS fault alarm | Boolean | 15146 | 0 | 315147.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15146_UPS_fault_alarm
133 | Available | Input Register | UPS bypass alarm | Boolean | 15146 | 1 | 315147.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15146_UPS_bypass_alarm
134 | Available | Input Register | UPS battery undervoltage alarm | Boolean | 15146 | 2 | 315147.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15146_UPS_battery_undervoltage_alarm
135 | Available | Input Register | UPS mains disconnection alarm | Boolean | 15146 | 4 | 315147.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15146_UPS_mains_disconnection_alarm
136 | Available | Input Register | U1 Daily power yield | 32-bit unsigned integer | 15149 |  | 315150 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15149_U1_Daily_power_yield_kWh
137 | Available | Input Register | U1 Monthly power yield | 32-bit unsigned integer | 15151 |  | 315152 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15151_U1_Monthly_power_yield_kWh |  | This point is not mapped to ignition
138 | Available | Input Register | U1 Total power yield | 32-bit unsigned integer | 15153 |  | 315154 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15153_U1_Total_power_yield_kWh
139 | Available | Input Register | U1 Daily grid connected minutes | 16-bit unsigned integer | 15155 |  | 315156 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15155_U1_Daily_grid_connected_minutes_min
140 | Available | Input Register | U1 Total running hours | 32-bit unsigned integer | 15156 |  | 315157 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15156_U1_Total_running_hours_hr
141 | Available | Input Register | U1 Internal Module Temperature | 16-bit signed integer | 15158 |  | 315159 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15158_U1_Internal_Module_Temperature_degC
142 | Available | Input Register | U1 DC Voltage | 16-bit unsigned integer | 15159 |  | 315160 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15159_U1_DC_Voltage_V
143 | Available | Input Register | U1 DC Current | 16-bit unsigned integer | 15160 |  | 315161 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15160_U1_DC_Current_A
144 | Available | Input Register | U1 DC Power | 32-bit signed integer | 15161 |  | 315162 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15161_U1_DC_Power_W
145 | Available | Input Register | U1 Voltage A-B | 16-bit unsigned integer | 15163 |  | 315164 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15163_U1_Voltage_A_B_V
146 | Available | Input Register | U1 Voltage B-C | 16-bit unsigned integer | 15164 |  | 315165 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15164_U1_Voltage_B_C_V
147 | Available | Input Register | U1 Voltage C-A | 16-bit unsigned integer | 15165 |  | 315166 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15165_U1_Voltage_C_A_V
148 | Available | Input Register | U1 Phase A Current | 16-bit unsigned integer | 15166 |  | 315167 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15166_U1_Phase_A_Current_A
149 | Available | Input Register | U1 Phase B Current | 16-bit unsigned integer | 15167 |  | 315168 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15167_U1_Phase_B_Current_A
150 | Available | Input Register | U1 Phase C Current | 16-bit unsigned integer | 15168 |  | 315169 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15168_U1_Phase_C_Current_A
151 | Available | Input Register | U1 Active Power | 32-bit signed integer | 15169 |  | 315170 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15169_U1_Active_Power_W
152 | Available | Input Register | U1 Reactive Power | 32-bit signed integer | 15171 |  | 315172 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15171_U1_Reactive_Power_var
153 | Available | Input Register | U1 Power Factor | 16-bit signed integer | 15173 |  | 315174 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15173_U1_Power_Factor_PU
154 | Available | Input Register | U1 Frequency | 16-bit unsigned integer | 15174 |  | 315175 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15174_U1_Frequency_Hz
155 | Available | Input Register | U1 Efficiency | 16-bit unsigned integer | 15175 |  | 315176 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15175_U1_Efficiency_pct
156 | Available | Input Register | U1 Clock Year | 16-bit unsigned integer | 15177 |  | 315178 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15177_U1_Clock_Year_year |  | This point is not mapped to ignition
157 | Available | Input Register | U1 Clock Month | 16-bit unsigned integer | 15178 |  | 315179 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15178_U1_Clock_Month_month |  | This point is not mapped to ignition
158 | Available | Input Register | U1 Clock Day | 16-bit unsigned integer | 15179 |  | 315180 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15179_U1_Clock_Day_day |  | This point is not mapped to ignition
159 | Available | Input Register | U1 Clock Hour | 16-bit unsigned integer | 15180 |  | 315181 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15180_U1_Clock_Hour_hr |  | This point is not mapped to ignition
160 | Available | Input Register | U1 Clock Minute | 16-bit unsigned integer | 15181 |  | 315182 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15181_U1_Clock_Minute_min |  | This point is not mapped to ignition
161 | Available | Input Register | U1 Clock Second | 16-bit unsigned integer | 15182 |  | 315183 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15182_U1_Clock_Second_s |  | This point is not mapped to ignition
162 | Available | Input Register | U1 Fault State 1 | 32-bit bitfield | 15185 |  | 315186 | [14 empty] | IREG_15185_U1_Fault_State_1
163 | Available | Input Register | U1 DC undervoltage alarm | Boolean | 15185 | 0 | 315186.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_undervoltage_alarm
164 | Available | Input Register | U1 DC overvoltage alarm | Boolean | 15185 | 1 | 315186.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_overvoltage_alarm
165 | Available | Input Register | U1 AC undervoltage alarm | Boolean | 15185 | 2 | 315186.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_undervoltage_alarm
166 | Available | Input Register | U1 AC overvoltage alarm | Boolean | 15185 | 3 | 315186.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_overvoltage_alarm
167 | Available | Input Register | U1 Anti islanding protection active | Boolean | 15185 | 7 | 315186.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Anti_islanding_protection_active
168 | Available | Input Register | U1 PDP protection active | Boolean | 15185 | 9 | 315186.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_PDP_protection_active
169 | Available | Input Register | U1 Module overtemperature alarm | Boolean | 15185 | 10 | 315186.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Module_overtemperature_alarm
170 | Available | Input Register | U1 Reactor overtemperature alarm | Boolean | 15185 | 11 | 315186.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Reactor_overtemperature_alarm
171 | Available | Input Register | U1 AC leakage current protection alarm | Boolean | 15185 | 14 | 315186.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_leakage_current_protection_alarm
172 | Available | Input Register | U1 GFDI protection active | Boolean | 15185 | 17 | 315186.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_GFDI_protection_active
173 | Available | Input Register | U1 Fan fault | Boolean | 15185 | 18 | 315186.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Fan_fault
174 | Available | Input Register | U1 DC overcurrent | Boolean | 15185 | 21 | 315186.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_DC_overcurrent
175 | Available | Input Register | U1 AC overcurrent | Boolean | 15185 | 22 | 315186.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_AC_overcurrent
176 | Available | Input Register | U1 Frequency abnormal | Boolean | 15185 | 23 | 315186.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Frequency_abnormal
177 | Available | Input Register | U1 Temperature abnormal | Boolean | 15185 | 24 | 315186.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Temperature_abnormal
178 | Available | Input Register | U1 Hardware fault | Boolean | 15185 | 25 | 315186.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Hardware_fault
179 | Available | Input Register | U1 Grounding fault | Boolean | 15185 | 26 | 315186.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Grounding_fault
180 | Available | Input Register | U1 Bus overvoltage | Boolean | 15185 | 27 | 315186.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Bus_overvoltage
181 | Available | Input Register | U1 Bus undervoltage | Boolean | 15185 | 28 | 315186.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Bus_undervoltage
182 | Available | Input Register | U1 Inverter overvoltage | Boolean | 15185 | 29 | 315186.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15185_U1_Inverter_overvoltage
183 | Available | Input Register | U1 Fault State 2 | 32-bit bitfield | 15187 |  | 315188 | [14 empty] | IREG_15187_U1_Fault_State_2
184 | Available | Input Register | U1 Insulation impedance fault | Boolean | 15187 | 0 | 315188.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Insulation_impedance_fault
185 | Available | Input Register | U1 AC SPD fault | Boolean | 15187 | 1 | 315188.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_SPD_fault
186 | Available | Input Register | U1 Sampling fault | Boolean | 15187 | 2 | 315188.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Sampling_fault
187 | Available | Input Register | U1 DC polarity reversed alarm | Boolean | 15187 | 3 | 315188.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_polarity_reversed_alarm
188 | Available | Input Register | U1 Control power supply fault | Boolean | 15187 | 4 | 315188.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Control_power_supply_fault
189 | Available | Input Register | U1 Backup power supply fault | Boolean | 15187 | 5 | 315188.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Backup_power_supply_fault
190 | Available | Input Register | U1 AC current imballance | Boolean | 15187 | 6 | 315188.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_current_imballance
191 | Available | Input Register | U1 AC fuse fault | Boolean | 15187 | 7 | 315188.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_fuse_fault
192 | Available | Input Register | U1 DC SPD fault | Boolean | 15187 | 8 | 315188.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_SPD_fault
193 | Available | Input Register | U1 Buffer contactor fault | Boolean | 15187 | 9 | 315188.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Buffer_contactor_fault
194 | Available | Input Register | U1 DC injection fault | Boolean | 15187 | 10 | 315188.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_injection_fault
195 | Available | Input Register | U1 DC switch fault | Boolean | 15187 | 11 | 315188.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_switch_fault
196 | Available | Input Register | U1 Device code repeat fault | Boolean | 15187 | 12 | 315188.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Device_code_repeat_fault
197 | Available | Input Register | U1 Parallel operation communication failure | Boolean | 15187 | 13 | 315188.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Parallel_operation_communication_failure
198 | Available | Input Register | U1 Control cabinet temperature alarm | Boolean | 15187 | 14 | 315188.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Control_cabinet_temperature_alarm
199 | Available | Input Register | U1 DC fuse grounding fault | Boolean | 15187 | 15 | 315188.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_fuse_grounding_fault
200 | Available | Input Register | U1 Reversed branch over current | Boolean | 15187 | 16 | 315188.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Reversed_branch_over_current
201 | Available | Input Register | U1 Grid voltage imballance | Boolean | 15187 | 17 | 315188.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Grid_voltage_imballance
202 | Available | Input Register | U1 inverter cabinet temperature alarm | Boolean | 15187 | 19 | 315188.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_inverter_cabinet_temperature_alarm
203 | Available | Input Register | U1 AC cabinet temperature alarm | Boolean | 15187 | 20 | 315188.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_cabinet_temperature_alarm
204 | Available | Input Register | U1 AC switch disconnection | Boolean | 15187 | 21 | 315188.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_switch_disconnection
205 | Available | Input Register | U1 AC switch fault | Boolean | 15187 | 22 | 315188.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_AC_switch_fault
206 | Available | Input Register | U1 Soft start fault | Boolean | 15187 | 23 | 315188.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Soft_start_fault
207 | Available | Input Register | U1 DC voltage sampling fault | Boolean | 15187 | 24 | 315188.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_voltage_sampling_fault
208 | Available | Input Register | U1 Fan 2 fault | Boolean | 15187 | 25 | 315188.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Fan_2_fault
209 | Available | Input Register | U1 Current unbalance 2 | Boolean | 15187 | 26 | 315188.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Current_unbalance_2
210 | Available | Input Register | U1 Current unbalance 3 | Boolean | 15187 | 27 | 315188.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Current_unbalance_3
211 | Available | Input Register | U1 DC cabinet temperature alarm | Boolean | 15187 | 29 | 315188.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_DC_cabinet_temperature_alarm
212 | Available | Input Register | U1 Neutral point potential shift alarm | Boolean | 15187 | 30 | 315188.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Neutral_point_potential_shift_alarm
213 | Available | Input Register | U1 Carrier sync failure | Boolean | 15187 | 31 | 315188.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15187_U1_Carrier_sync_failure
214 | Available | Input Register | U1 Fault State 3 | 32-bit bitfield | 15189 |  | 315190 | [14 empty] | IREG_15189_U1_Fault_State_3
215 | Available | Input Register | U1 smoke sensing fault | Boolean | 15189 | 0 | 315190.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15189_U1_smoke_sensing_fault
216 | Available | Input Register | U1 access control fault | Boolean | 15189 | 1 | 315190.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15189_U1_access_control_fault
217 | Available | Input Register | U1 Emergency fault shutdown fault | Boolean | 15189 | 2 | 315190.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15189_U1_Emergency_fault_shutdown_fault
218 | Available | Input Register | U1 Node State 1 | 32-bit bitfield | 15193 |  | 315194 | [14 empty] | IREG_15193_U1_Node_State_1
219 | Available | Input Register | U1 AC circuit breaker status | Boolean | 15193 | 0 | 315194.0 |  | None | Closed | Open | [10 empty] | IREG_15193_U1_AC_circuit_breaker_status
220 | Available | Input Register | U1 DC switch 1 status | Boolean | 15193 | 3 | 315194.3 |  | None | Closed | Open | [10 empty] | IREG_15193_U1_DC_switch_1_status
221 | Available | Input Register | U1 smoke node status | Boolean | 15193 | 17 | 315194.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15193_U1_smoke_node_status
222 | Available | Input Register | U1 access node status | Boolean | 15193 | 18 | 315194.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15193_U1_access_node_status
223 | Available | Input Register | U1 emergency shutdown status | Boolean | 15193 | 19 | 315194.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15193_U1_emergency_shutdown_status
224 | Available | Input Register | U1 Temperature 1 | 16-bit signed integer | 15197 |  | 315198 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15197_U1_Temperature_1_degC
225 | Available | Input Register | U1 Temperature 3 | 16-bit signed integer | 15199 |  | 315200 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15199_U1_Temperature_3_degC
226 | Available | Input Register | U1 Temperature 5 | 16-bit signed integer | 15201 |  | 315202 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15201_U1_Temperature_5_degC
227 | Available | Input Register | U1 Positive Resistance to Ground | 32-bit unsigned integer | 15203 |  | 315204 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15203_U1_Positive_Resistance_to_Ground_kOhm
228 | Available | Input Register | U1 Negative Resistance to Ground | 32-bit unsigned integer | 15205 |  | 315206 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15205_U1_Negative_Resistance_to_Ground_kOhm
229 | Available | Input Register | U1 Work State | 32-bit bitfield | 15207 |  | 315208 | [14 empty] | IREG_15207_U1_Work_State
230 | Available | Input Register | U1 Running | Boolean | 15207 | 0 | 315208.0 |  | None | Running | Not Running | [10 empty] | IREG_15207_U1_Running
231 | Available | Input Register | U1 Stopped | Boolean | 15207 | 1 | 315208.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15207_U1_Stopped
232 | Available | Input Register | U1 Initial Standby | Boolean | 15207 | 2 | 315208.2 |  | None | Standby | Not Standby | [10 empty] | IREG_15207_U1_Initial_Standby
233 | Available | Input Register | U1 Press to shutdown | Boolean | 15207 | 3 | 315208.3 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15207_U1_Press_to_shutdown
234 | Available | Input Register | U1 Standby | Boolean | 15207 | 4 | 315208.4 |  | None | Standby | Not Standby | [10 empty] | IREG_15207_U1_Standby
235 | Available | Input Register | U1 Emergency Stop | Boolean | 15207 | 5 | 315208.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Emergency_Stop
236 | Available | Input Register | U1 Starting | Boolean | 15207 | 6 | 315208.6 |  | None | Starting | Not Starting | [10 empty] | IREG_15207_U1_Starting
237 | Available | Input Register | U1 Stopping | Boolean | 15207 | 7 | 315208.7 |  | None | Stopping | Not Stopping | [10 empty] | IREG_15207_U1_Stopping
238 | Available | Input Register | U1 Fault Stop | Boolean | 15207 | 9 | 315208.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Fault_Stop
239 | Available | Input Register | U1 Alarm running | Boolean | 15207 | 10 | 315208.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Alarm_running
240 | Available | Input Register | U1 Derating running | Boolean | 15207 | 11 | 315208.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_Derating_running
241 | Available | Input Register | U1 IO-DSP communication failure | Boolean | 15207 | 13 | 315208.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15207_U1_IO_DSP_communication_failure
242 | Available | Input Register | U1 Inverter is running | Boolean | 15207 | 17 | 315208.17 |  | None | Running | Not Running | [10 empty] | IREG_15207_U1_Inverter_is_running
243 | Available | Input Register | U1 Inverter is stopped | Boolean | 15207 | 18 | 315208.18 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15207_U1_Inverter_is_stopped
244 | Available | Input Register | U1 Anti-PID active | Boolean | 15207 | 19 | 315208.19 |  | On (1) | Active | Not-Active | [10 empty] | IREG_15207_U1_Anti_PID_active
245 | Available | Input Register | U1 Alarm State | 32-bit bitfield | 15209 |  | 315210 | [14 empty] | IREG_15209_U1_Alarm_State
246 | Available | Input Register | U1 Temperature alarm | Boolean | 15209 | 0 | 315210.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Temperature_alarm
247 | Available | Input Register | U1 Low insulation resistance alarm | Boolean | 15209 | 1 | 315210.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Low_insulation_resistance_alarm
248 | Available | Input Register | U1 GFRT operation alarm | Boolean | 15209 | 2 | 315210.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_GFRT_operation_alarm
249 | Available | Input Register | U1 CT unbalance | Boolean | 15209 | 3 | 315210.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_CT_unbalance
250 | Available | Input Register | U1 DC sensor fault | Boolean | 15209 | 6 | 315210.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_sensor_fault
251 | Available | Input Register | U1 DC SPD fault | Boolean | 15209 | 7 | 315210.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_SPD_fault
252 | Available | Input Register | U1 AC SPD fault | Boolean | 15209 | 8 | 315210.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_AC_SPD_fault
253 | Available | Input Register | U1 DC switch fault | Boolean | 15209 | 12 | 315210.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_switch_fault
254 | Available | Input Register | U1 Anti-PID power supply | Boolean | 15209 | 13 | 315210.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Anti_PID_power_supply
255 | Available | Input Register | U1 Fan fault | Boolean | 15209 | 14 | 315210.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Fan_fault
256 | Available | Input Register | U1 DC bypass forward overcurrent alarm | Boolean | 15209 | 16 | 315210.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_bypass_forward_overcurrent_alarm
257 | Available | Input Register | U1 DC bypass reverse overcurrent alarm | Boolean | 15209 | 17 | 315210.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_DC_bypass_reverse_overcurrent_alarm
258 | Available | Input Register | U1 AC circuit breaker fault | Boolean | 15209 | 19 | 315210.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_AC_circuit_breaker_fault
259 | Available | Input Register | U1 Meter communication failure | Boolean | 15209 | 20 | 315210.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Meter_communication_failure
260 | Available | Input Register | U1 Fan 2 fault | Boolean | 15209 | 21 | 315210.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Fan_2_fault
261 | Available | Input Register | U1 Temperature and humidity sensor fault | Boolean | 15209 | 23 | 315210.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Temperature_and_humidity_sensor_fault
262 | Available | Input Register | U1 Frequency deviation active power regulation | Boolean | 15209 | 24 | 315210.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Frequency_deviation_active_power_regulation
263 | Available | Input Register | U1 Voltage deviation reactive power regulation | Boolean | 15209 | 25 | 315210.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Voltage_deviation_reactive_power_regulation
264 | Available | Input Register | U1 Busbar temperature alarm | Boolean | 15209 | 27 | 315210.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Busbar_temperature_alarm
265 | Available | Input Register | U1 Abnormal derating of fan | Boolean | 15209 | 28 | 315210.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Abnormal_derating_of_fan
266 | Available | Input Register | U1 Frequency abnormal | Boolean | 15209 | 30 | 315210.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15209_U1_Frequency_abnormal
267 | Available | Input Register | U1 Negative Voltage to Ground | 16-bit signed integer | 15211 |  | 315212 |  |  |  |  | V | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15211_U1_Negative_Voltage_to_Ground_V
268 | Available | Input Register | U1 Annual Power Yield | 32-bit unsigned integer | 15212 |  | 315213 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15212_U1_Annual_Power_Yield_kWh |  | This point is not mapped to ignition
269 | Available | Input Register | U1 CO2 Emission Reduction | 32-bit unsigned integer | 15214 |  | 315215 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15214_U1_CO2_Emission_Reduction_kg |  | This point is not mapped to ignition
270 | Available | Input Register | U1 leakage current | 16-bit unsigned integer | 15236 |  | 315237 |  |  |  |  | A | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15236_U1_leakage_current_A
271 | Available | Input Register | U1 DC Input #1 | 16-bit signed integer | 15249 |  | 315250 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15249_U1_DC_Input_1_A
272 | Available | Input Register | U1 DC Input #2 | 16-bit signed integer | 15250 |  | 315251 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15250_U1_DC_Input_2_A
273 | Available | Input Register | U1 DC Input #3 | 16-bit signed integer | 15251 |  | 315252 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15251_U1_DC_Input_3_A
274 | Available | Input Register | U1 DC Input #4 | 16-bit signed integer | 15252 |  | 315253 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15252_U1_DC_Input_4_A
275 | Available | Input Register | U1 DC Input #5 | 16-bit signed integer | 15253 |  | 315254 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15253_U1_DC_Input_5_A
276 | Available | Input Register | U1 DC Input #6 | 16-bit signed integer | 15254 |  | 315255 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15254_U1_DC_Input_6_A
277 | Available | Input Register | U1 DC Input #7 | 16-bit signed integer | 15255 |  | 315256 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15255_U1_DC_Input_7_A
278 | Available | Input Register | U1 running status | 16-bit bitfield | 15261 |  | 315262 | [14 empty] | IREG_15261_U1_running_status
279 | Available | Input Register | U1 HVRT operation | Boolean | 15261 | 1 | 315262.1 |  | None | On | Off | [10 empty] | IREG_15261_U1_HVRT_operation
280 | Available | Input Register | U1 LVRT operation | Boolean | 15261 | 2 | 315262.2 |  | None | On | Off | [10 empty] | IREG_15261_U1_LVRT_operation
281 | Available | Input Register | U2 Daily power yield | 32-bit unsigned integer | 15269 |  | 315270 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15269_U2_Daily_power_yield_kWh
282 | Available | Input Register | U2 Monthly power yield | 32-bit unsigned integer | 15271 |  | 315272 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15271_U2_Monthly_power_yield_kWh |  | This point is not mapped to ignition
283 | Available | Input Register | U2 Total power yield | 32-bit unsigned integer | 15273 |  | 315274 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15273_U2_Total_power_yield_kWh
284 | Available | Input Register | U2 Daily grid connected minutes | 16-bit unsigned integer | 15275 |  | 315276 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15275_U2_Daily_grid_connected_minutes_min
285 | Available | Input Register | U2 Total running hours | 32-bit unsigned integer | 15276 |  | 315277 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15276_U2_Total_running_hours_hr
286 | Available | Input Register | U2 Internal Module Temperature | 16-bit signed integer | 15278 |  | 315279 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15278_U2_Internal_Module_Temperature_degC
287 | Available | Input Register | U2 DC Voltage | 16-bit unsigned integer | 15279 |  | 315280 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15279_U2_DC_Voltage_V
288 | Available | Input Register | U2 DC Current | 16-bit unsigned integer | 15280 |  | 315281 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15280_U2_DC_Current_A
289 | Available | Input Register | U2 DC Power | 32-bit signed integer | 15281 |  | 315282 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15281_U2_DC_Power_W
290 | Available | Input Register | U2 Voltage A-B | 16-bit unsigned integer | 15283 |  | 315284 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15283_U2_Voltage_A_B_V
291 | Available | Input Register | U2 Voltage B-C | 16-bit unsigned integer | 15284 |  | 315285 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15284_U2_Voltage_B_C_V
292 | Available | Input Register | U2 Voltage C-A | 16-bit unsigned integer | 15285 |  | 315286 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15285_U2_Voltage_C_A_V
293 | Available | Input Register | U2 Phase A Current | 16-bit unsigned integer | 15286 |  | 315287 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15286_U2_Phase_A_Current_A
294 | Available | Input Register | U2 Phase B Current | 16-bit unsigned integer | 15287 |  | 315288 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15287_U2_Phase_B_Current_A
295 | Available | Input Register | U2 Phase C Current | 16-bit unsigned integer | 15288 |  | 315289 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15288_U2_Phase_C_Current_A
296 | Available | Input Register | U2 Active Power | 32-bit signed integer | 15289 |  | 315290 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15289_U2_Active_Power_W
297 | Available | Input Register | U2 Reactive Power | 32-bit signed integer | 15291 |  | 315292 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15291_U2_Reactive_Power_var
298 | Available | Input Register | U2 Power Factor | 16-bit signed integer | 15293 |  | 315294 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15293_U2_Power_Factor_PU
299 | Available | Input Register | U2 Frequency | 16-bit unsigned integer | 15294 |  | 315295 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15294_U2_Frequency_Hz
300 | Available | Input Register | U2 Efficiency | 16-bit unsigned integer | 15295 |  | 315296 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15295_U2_Efficiency_pct
301 | Available | Input Register | U2 Clock Year | 16-bit unsigned integer | 15297 |  | 315298 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15297_U2_Clock_Year_year |  | This point is not mapped to ignition
302 | Available | Input Register | U2 Clock Month | 16-bit unsigned integer | 15298 |  | 315299 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15298_U2_Clock_Month_month |  | This point is not mapped to ignition
303 | Available | Input Register | U2 Clock Day | 16-bit unsigned integer | 15299 |  | 315300 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15299_U2_Clock_Day_day |  | This point is not mapped to ignition
304 | Available | Input Register | U2 Clock Hour | 16-bit unsigned integer | 15300 |  | 315301 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15300_U2_Clock_Hour_hr |  | This point is not mapped to ignition
305 | Available | Input Register | U2 Clock Minute | 16-bit unsigned integer | 15301 |  | 315302 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15301_U2_Clock_Minute_min |  | This point is not mapped to ignition
306 | Available | Input Register | U2 Clock Second | 16-bit unsigned integer | 15302 |  | 315303 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15302_U2_Clock_Second_s |  | This point is not mapped to ignition
307 | Available | Input Register | U2 Fault State 1 | 32-bit bitfield | 15305 |  | 315306 | [14 empty] | IREG_15305_U2_Fault_State_1
308 | Available | Input Register | U2 DC undervoltage alarm | Boolean | 15305 | 0 | 315306.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_undervoltage_alarm
309 | Available | Input Register | U2 DC overvoltage alarm | Boolean | 15305 | 1 | 315306.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_overvoltage_alarm
310 | Available | Input Register | U2 AC undervoltage alarm | Boolean | 15305 | 2 | 315306.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_undervoltage_alarm
311 | Available | Input Register | U2 AC overvoltage alarm | Boolean | 15305 | 3 | 315306.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_overvoltage_alarm
312 | Available | Input Register | U2 Anti islanding protection active | Boolean | 15305 | 7 | 315306.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Anti_islanding_protection_active
313 | Available | Input Register | U2 PDP protection active | Boolean | 15305 | 9 | 315306.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_PDP_protection_active
314 | Available | Input Register | U2 Module overtemperature alarm | Boolean | 15305 | 10 | 315306.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Module_overtemperature_alarm
315 | Available | Input Register | U2 Reactor overtemperature alarm | Boolean | 15305 | 11 | 315306.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Reactor_overtemperature_alarm
316 | Available | Input Register | U2 AC leakage current protection alarm | Boolean | 15305 | 14 | 315306.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_leakage_current_protection_alarm
317 | Available | Input Register | U2 GFDI protection active | Boolean | 15305 | 17 | 315306.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_GFDI_protection_active
318 | Available | Input Register | U2 Fan fault | Boolean | 15305 | 18 | 315306.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Fan_fault
319 | Available | Input Register | U2 DC overcurrent | Boolean | 15305 | 21 | 315306.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_DC_overcurrent
320 | Available | Input Register | U2 AC overcurrent | Boolean | 15305 | 22 | 315306.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_AC_overcurrent
321 | Available | Input Register | U2 Frequency abnormal | Boolean | 15305 | 23 | 315306.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Frequency_abnormal
322 | Available | Input Register | U2 Temperature abnormal | Boolean | 15305 | 24 | 315306.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Temperature_abnormal
323 | Available | Input Register | U2 Hardware fault | Boolean | 15305 | 25 | 315306.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Hardware_fault
324 | Available | Input Register | U2 Grounding fault | Boolean | 15305 | 26 | 315306.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Grounding_fault
325 | Available | Input Register | U2 Bus overvoltage | Boolean | 15305 | 27 | 315306.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Bus_overvoltage
326 | Available | Input Register | U2 Bus undervoltage | Boolean | 15305 | 28 | 315306.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Bus_undervoltage
327 | Available | Input Register | U2 Inverter overvoltage | Boolean | 15305 | 29 | 315306.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15305_U2_Inverter_overvoltage
328 | Available | Input Register | U2 Fault State 2 | 32-bit bitfield | 15307 |  | 315308 | [14 empty] | IREG_15307_U2_Fault_State_2
329 | Available | Input Register | U2 Insulation impedance fault | Boolean | 15307 | 0 | 315308.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Insulation_impedance_fault
330 | Available | Input Register | U2 AC SPD fault | Boolean | 15307 | 1 | 315308.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_SPD_fault
331 | Available | Input Register | U2 Sampling fault | Boolean | 15307 | 2 | 315308.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Sampling_fault
332 | Available | Input Register | U2 DC polarity reversed alarm | Boolean | 15307 | 3 | 315308.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_polarity_reversed_alarm
333 | Available | Input Register | U2 Control power supply fault | Boolean | 15307 | 4 | 315308.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Control_power_supply_fault
334 | Available | Input Register | U2 Backup power supply fault | Boolean | 15307 | 5 | 315308.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Backup_power_supply_fault
335 | Available | Input Register | U2 AC current imballance | Boolean | 15307 | 6 | 315308.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_current_imballance
336 | Available | Input Register | U2 AC fuse fault | Boolean | 15307 | 7 | 315308.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_fuse_fault
337 | Available | Input Register | U2 DC SPD fault | Boolean | 15307 | 8 | 315308.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_SPD_fault
338 | Available | Input Register | U2 Buffer contactor fault | Boolean | 15307 | 9 | 315308.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Buffer_contactor_fault
339 | Available | Input Register | U2 DC injection fault | Boolean | 15307 | 10 | 315308.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_injection_fault
340 | Available | Input Register | U2 DC switch fault | Boolean | 15307 | 11 | 315308.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_switch_fault
341 | Available | Input Register | U2 Device code repeat fault | Boolean | 15307 | 12 | 315308.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Device_code_repeat_fault
342 | Available | Input Register | U2 Parallel operation communication failure | Boolean | 15307 | 13 | 315308.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Parallel_operation_communication_failure
343 | Available | Input Register | U2 Control cabinet temperature alarm | Boolean | 15307 | 14 | 315308.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Control_cabinet_temperature_alarm
344 | Available | Input Register | U2 DC fuse grounding fault | Boolean | 15307 | 15 | 315308.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_fuse_grounding_fault
345 | Available | Input Register | U2 Reversed branch over current | Boolean | 15307 | 16 | 315308.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Reversed_branch_over_current
346 | Available | Input Register | U2 Grid voltage imballance | Boolean | 15307 | 17 | 315308.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Grid_voltage_imballance
347 | Available | Input Register | U2 inverter cabinet temperature alarm | Boolean | 15307 | 19 | 315308.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_inverter_cabinet_temperature_alarm
348 | Available | Input Register | U2 AC cabinet temperature alarm | Boolean | 15307 | 20 | 315308.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_cabinet_temperature_alarm
349 | Available | Input Register | U2 AC switch disconnection | Boolean | 15307 | 21 | 315308.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_switch_disconnection
350 | Available | Input Register | U2 AC switch fault | Boolean | 15307 | 22 | 315308.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_AC_switch_fault
351 | Available | Input Register | U2 Soft start fault | Boolean | 15307 | 23 | 315308.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Soft_start_fault
352 | Available | Input Register | U2 DC voltage sampling fault | Boolean | 15307 | 24 | 315308.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_voltage_sampling_fault
353 | Available | Input Register | U2 Fan 2 fault | Boolean | 15307 | 25 | 315308.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Fan_2_fault
354 | Available | Input Register | U2 Current unbalance 2 | Boolean | 15307 | 26 | 315308.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Current_unbalance_2
355 | Available | Input Register | U2 Current unbalance 3 | Boolean | 15307 | 27 | 315308.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Current_unbalance_3
356 | Available | Input Register | U2 DC cabinet temperature alarm | Boolean | 15307 | 29 | 315308.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_DC_cabinet_temperature_alarm
357 | Available | Input Register | U2 Neutral point potential shift alarm | Boolean | 15307 | 30 | 315308.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Neutral_point_potential_shift_alarm
358 | Available | Input Register | U2 Carrier sync failure | Boolean | 15307 | 31 | 315308.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15307_U2_Carrier_sync_failure
359 | Available | Input Register | U2 Fault State 3 | 32-bit bitfield | 15309 |  | 315310 | [14 empty] | IREG_15309_U2_Fault_State_3
360 | Available | Input Register | U2 smoke sensing fault | Boolean | 15309 | 0 | 315310.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15309_U2_smoke_sensing_fault
361 | Available | Input Register | U2 access control fault | Boolean | 15309 | 1 | 315310.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15309_U2_access_control_fault
362 | Available | Input Register | U2 Emergency fault shutdown fault | Boolean | 15309 | 2 | 315310.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15309_U2_Emergency_fault_shutdown_fault
363 | Available | Input Register | U2 Node State 1 | 32-bit bitfield | 15313 |  | 315314 | [14 empty] | IREG_15313_U2_Node_State_1
364 | Available | Input Register | U2 AC circuit breaker status | Boolean | 15313 | 0 | 315314.0 |  | None | Closed | Open | [10 empty] | IREG_15313_U2_AC_circuit_breaker_status
365 | Available | Input Register | U2 DC switch 1 status | Boolean | 15313 | 3 | 315314.3 |  | None | Closed | Open | [10 empty] | IREG_15313_U2_DC_switch_1_status
366 | Available | Input Register | U2 smoke node status | Boolean | 15313 | 17 | 315314.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15313_U2_smoke_node_status
367 | Available | Input Register | U2 access node status | Boolean | 15313 | 18 | 315314.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15313_U2_access_node_status
368 | Available | Input Register | U2 emergency shutdown status | Boolean | 15313 | 19 | 315314.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15313_U2_emergency_shutdown_status
369 | Available | Input Register | U2 Temperature 1 | 16-bit signed integer | 15317 |  | 315318 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15317_U2_Temperature_1_degC
370 | Available | Input Register | U2 Temperature 3 | 16-bit signed integer | 15319 |  | 315320 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15319_U2_Temperature_3_degC
371 | Available | Input Register | U2 Temperature 5 | 16-bit signed integer | 15321 |  | 315322 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15321_U2_Temperature_5_degC
372 | Available | Input Register | U2 Positive Resistance to Ground | 32-bit unsigned integer | 15323 |  | 315324 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15323_U2_Positive_Resistance_to_Ground_kOhm
373 | Available | Input Register | U2 Negative Resistance to Ground | 32-bit unsigned integer | 15325 |  | 315326 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15325_U2_Negative_Resistance_to_Ground_kOhm
374 | Available | Input Register | U2 Work State | 32-bit bitfield | 15327 |  | 315328 | [14 empty] | IREG_15327_U2_Work_State
375 | Available | Input Register | U2 Running | Boolean | 15327 | 0 | 315328.0 |  | None | Running | Not Running | [10 empty] | IREG_15327_U2_Running
376 | Available | Input Register | U2 Stopped | Boolean | 15327 | 1 | 315328.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15327_U2_Stopped
377 | Available | Input Register | U2 Initial Standby | Boolean | 15327 | 2 | 315328.2 |  | None | Standby | Not Standby | [10 empty] | IREG_15327_U2_Initial_Standby
378 | Available | Input Register | U2 Press to shutdown | Boolean | 15327 | 3 | 315328.3 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15327_U2_Press_to_shutdown
379 | Available | Input Register | U2 Standby | Boolean | 15327 | 4 | 315328.4 |  | None | Standby | Not Standby | [10 empty] | IREG_15327_U2_Standby
380 | Available | Input Register | U2 Emergency Stop | Boolean | 15327 | 5 | 315328.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Emergency_Stop
381 | Available | Input Register | U2 Starting | Boolean | 15327 | 6 | 315328.6 |  | None | Starting | Not Starting | [10 empty] | IREG_15327_U2_Starting
382 | Available | Input Register | U2 Stopping | Boolean | 15327 | 7 | 315328.7 |  | None | Stopping | Not Stopping | [10 empty] | IREG_15327_U2_Stopping
383 | Available | Input Register | U2 Fault Stop | Boolean | 15327 | 9 | 315328.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Fault_Stop
384 | Available | Input Register | U2 Alarm running | Boolean | 15327 | 10 | 315328.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Alarm_running
385 | Available | Input Register | U2 Derating running | Boolean | 15327 | 11 | 315328.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_Derating_running
386 | Available | Input Register | U2 IO-DSP communication failure | Boolean | 15327 | 13 | 315328.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15327_U2_IO_DSP_communication_failure
387 | Available | Input Register | U2 Inverter is running | Boolean | 15327 | 17 | 315328.17 |  | None | Running | Not Running | [10 empty] | IREG_15327_U2_Inverter_is_running
388 | Available | Input Register | U2 Inverter is stopped | Boolean | 15327 | 18 | 315328.18 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15327_U2_Inverter_is_stopped
389 | Available | Input Register | U2 Anti-PID active | Boolean | 15327 | 19 | 315328.19 |  | On (1) | Active | Not-Active | [10 empty] | IREG_15327_U2_Anti_PID_active
390 | Available | Input Register | U2 Alarm State | 32-bit bitfield | 15329 |  | 315330 | [14 empty] | IREG_15329_U2_Alarm_State
391 | Available | Input Register | U2 Temperature alarm | Boolean | 15329 | 0 | 315330.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Temperature_alarm
392 | Available | Input Register | U2 Low insulation resistance alarm | Boolean | 15329 | 1 | 315330.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Low_insulation_resistance_alarm
393 | Available | Input Register | U2 GFRT operation alarm | Boolean | 15329 | 2 | 315330.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_GFRT_operation_alarm
394 | Available | Input Register | U2 CT unbalance | Boolean | 15329 | 3 | 315330.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_CT_unbalance
395 | Available | Input Register | U2 DC sensor fault | Boolean | 15329 | 6 | 315330.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_sensor_fault
396 | Available | Input Register | U2 DC SPD fault | Boolean | 15329 | 7 | 315330.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_SPD_fault
397 | Available | Input Register | U2 AC SPD fault | Boolean | 15329 | 8 | 315330.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_AC_SPD_fault
398 | Available | Input Register | U2 DC switch fault | Boolean | 15329 | 12 | 315330.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_switch_fault
399 | Available | Input Register | U2 Anti-PID power supply | Boolean | 15329 | 13 | 315330.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Anti_PID_power_supply
400 | Available | Input Register | U2 Fan fault | Boolean | 15329 | 14 | 315330.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Fan_fault
401 | Available | Input Register | U2 DC bypass forward overcurrent alarm | Boolean | 15329 | 16 | 315330.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_bypass_forward_overcurrent_alarm
402 | Available | Input Register | U2 DC bypass reverse overcurrent alarm | Boolean | 15329 | 17 | 315330.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_DC_bypass_reverse_overcurrent_alarm
403 | Available | Input Register | U2 AC circuit breaker fault | Boolean | 15329 | 19 | 315330.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_AC_circuit_breaker_fault
404 | Available | Input Register | U2 Meter communication failure | Boolean | 15329 | 20 | 315330.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Meter_communication_failure
405 | Available | Input Register | U2 Fan 2 fault | Boolean | 15329 | 21 | 315330.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Fan_2_fault
406 | Available | Input Register | U2 Temperature and humidity sensor fault | Boolean | 15329 | 23 | 315330.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Temperature_and_humidity_sensor_fault
407 | Available | Input Register | U2 Frequency deviation active power regulation | Boolean | 15329 | 24 | 315330.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Frequency_deviation_active_power_regulation
408 | Available | Input Register | U2 Voltage deviation reactive power regulation | Boolean | 15329 | 25 | 315330.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Voltage_deviation_reactive_power_regulation
409 | Available | Input Register | U2 Busbar temperature alarm | Boolean | 15329 | 27 | 315330.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Busbar_temperature_alarm
410 | Available | Input Register | U2 Abnormal derating of fan | Boolean | 15329 | 28 | 315330.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Abnormal_derating_of_fan
411 | Available | Input Register | U2 Frequency abnormal | Boolean | 15329 | 30 | 315330.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15329_U2_Frequency_abnormal
412 | Available | Input Register | U2 Negative Voltage to Ground | 16-bit signed integer | 15331 |  | 315332 |  |  |  |  | V | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15331_U2_Negative_Voltage_to_Ground_V
413 | Available | Input Register | U2 Annual Power Yield | 32-bit unsigned integer | 15332 |  | 315333 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15332_U2_Annual_Power_Yield_kWh |  | This point is not mapped to ignition
414 | Available | Input Register | U2 CO2 Emission Reduction | 32-bit unsigned integer | 15334 |  | 315335 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15334_U2_CO2_Emission_Reduction_kg |  | This point is not mapped to ignition
415 | Available | Input Register | U2 leakage current | 16-bit unsigned integer | 15356 |  | 315357 |  |  |  |  | A | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15356_U2_leakage_current_A
416 | Available | Input Register | U2 DC Input #1 | 16-bit signed integer | 15369 |  | 315370 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15369_U2_DC_Input_1_A
417 | Available | Input Register | U2 DC Input #2 | 16-bit signed integer | 15370 |  | 315371 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15370_U2_DC_Input_2_A
418 | Available | Input Register | U2 DC Input #3 | 16-bit signed integer | 15371 |  | 315372 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15371_U2_DC_Input_3_A
419 | Available | Input Register | U2 DC Input #4 | 16-bit signed integer | 15372 |  | 315373 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15372_U2_DC_Input_4_A
420 | Available | Input Register | U2 DC Input #5 | 16-bit signed integer | 15373 |  | 315374 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15373_U2_DC_Input_5_A
421 | Available | Input Register | U2 DC Input #6 | 16-bit signed integer | 15374 |  | 315375 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15374_U2_DC_Input_6_A
422 | Available | Input Register | U2 DC Input #7 | 16-bit signed integer | 15375 |  | 315376 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15375_U2_DC_Input_7_A
423 | Available | Input Register | U2 running status | 16-bit bitfield | 15381 |  | 315382 | [14 empty] | IREG_15381_U2_running_status
424 | Available | Input Register | U2 HVRT operation | Boolean | 15381 | 1 | 315382.1 |  | None | On | Off | [10 empty] | IREG_15381_U2_HVRT_operation
425 | Available | Input Register | U2 LVRT operation | Boolean | 15381 | 2 | 315382.2 |  | None | On | Off | [10 empty] | IREG_15381_U2_LVRT_operation
426 | Available | Input Register | U3 Daily power yield | 32-bit unsigned integer | 15389 |  | 315390 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15389_U3_Daily_power_yield_kWh
427 | Available | Input Register | U3 Monthly power yield | 32-bit unsigned integer | 15391 |  | 315392 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15391_U3_Monthly_power_yield_kWh |  | This point is not mapped to ignition
428 | Available | Input Register | U3 Total power yield | 32-bit unsigned integer | 15393 |  | 315394 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15393_U3_Total_power_yield_kWh
429 | Available | Input Register | U3 Daily grid connected minutes | 16-bit unsigned integer | 15395 |  | 315396 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15395_U3_Daily_grid_connected_minutes_min
430 | Available | Input Register | U3 Total running hours | 32-bit unsigned integer | 15396 |  | 315397 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15396_U3_Total_running_hours_hr
431 | Available | Input Register | U3 Internal Module Temperature | 16-bit signed integer | 15398 |  | 315399 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15398_U3_Internal_Module_Temperature_degC
432 | Available | Input Register | U3 DC Voltage | 16-bit unsigned integer | 15399 |  | 315400 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15399_U3_DC_Voltage_V
433 | Available | Input Register | U3 DC Current | 16-bit unsigned integer | 15400 |  | 315401 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15400_U3_DC_Current_A
434 | Available | Input Register | U3 DC Power | 32-bit signed integer | 15401 |  | 315402 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15401_U3_DC_Power_W
435 | Available | Input Register | U3 Voltage A-B | 16-bit unsigned integer | 15403 |  | 315404 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15403_U3_Voltage_A_B_V
436 | Available | Input Register | U3 Voltage B-C | 16-bit unsigned integer | 15404 |  | 315405 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15404_U3_Voltage_B_C_V
437 | Available | Input Register | U3 Voltage C-A | 16-bit unsigned integer | 15405 |  | 315406 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15405_U3_Voltage_C_A_V
438 | Available | Input Register | U3 Phase A Current | 16-bit unsigned integer | 15406 |  | 315407 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15406_U3_Phase_A_Current_A
439 | Available | Input Register | U3 Phase B Current | 16-bit unsigned integer | 15407 |  | 315408 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15407_U3_Phase_B_Current_A
440 | Available | Input Register | U3 Phase C Current | 16-bit unsigned integer | 15408 |  | 315409 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15408_U3_Phase_C_Current_A
441 | Available | Input Register | U3 Active Power | 32-bit signed integer | 15409 |  | 315410 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15409_U3_Active_Power_W
442 | Available | Input Register | U3 Reactive Power | 32-bit signed integer | 15411 |  | 315412 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15411_U3_Reactive_Power_var
443 | Available | Input Register | U3 Power Factor | 16-bit signed integer | 15413 |  | 315414 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15413_U3_Power_Factor_PU
444 | Available | Input Register | U3 Frequency | 16-bit unsigned integer | 15414 |  | 315415 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15414_U3_Frequency_Hz
445 | Available | Input Register | U3 Efficiency | 16-bit unsigned integer | 15415 |  | 315416 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15415_U3_Efficiency_pct
446 | Available | Input Register | U3 Clock Year | 16-bit unsigned integer | 15417 |  | 315418 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15417_U3_Clock_Year_year |  | This point is not mapped to ignition
447 | Available | Input Register | U3 Clock Month | 16-bit unsigned integer | 15418 |  | 315419 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15418_U3_Clock_Month_month |  | This point is not mapped to ignition
448 | Available | Input Register | U3 Clock Day | 16-bit unsigned integer | 15419 |  | 315420 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15419_U3_Clock_Day_day |  | This point is not mapped to ignition
449 | Available | Input Register | U3 Clock Hour | 16-bit unsigned integer | 15420 |  | 315421 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15420_U3_Clock_Hour_hr |  | This point is not mapped to ignition
450 | Available | Input Register | U3 Clock Minute | 16-bit unsigned integer | 15421 |  | 315422 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15421_U3_Clock_Minute_min |  | This point is not mapped to ignition
451 | Available | Input Register | U3 Clock Second | 16-bit unsigned integer | 15422 |  | 315423 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15422_U3_Clock_Second_s |  | This point is not mapped to ignition
452 | Available | Input Register | U3 Fault State 1 | 32-bit bitfield | 15425 |  | 315426 | [14 empty] | IREG_15425_U3_Fault_State_1
453 | Available | Input Register | U3 DC undervoltage alarm | Boolean | 15425 | 0 | 315426.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_DC_undervoltage_alarm
454 | Available | Input Register | U3 DC overvoltage alarm | Boolean | 15425 | 1 | 315426.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_DC_overvoltage_alarm
455 | Available | Input Register | U3 AC undervoltage alarm | Boolean | 15425 | 2 | 315426.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_AC_undervoltage_alarm
456 | Available | Input Register | U3 AC overvoltage alarm | Boolean | 15425 | 3 | 315426.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_AC_overvoltage_alarm
457 | Available | Input Register | U3 Anti islanding protection active | Boolean | 15425 | 7 | 315426.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Anti_islanding_protection_active
458 | Available | Input Register | U3 PDP protection active | Boolean | 15425 | 9 | 315426.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_PDP_protection_active
459 | Available | Input Register | U3 Module overtemperature alarm | Boolean | 15425 | 10 | 315426.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Module_overtemperature_alarm
460 | Available | Input Register | U3 Reactor overtemperature alarm | Boolean | 15425 | 11 | 315426.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Reactor_overtemperature_alarm
461 | Available | Input Register | U3 AC leakage current protection alarm | Boolean | 15425 | 14 | 315426.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_AC_leakage_current_protection_alarm
462 | Available | Input Register | U3 GFDI protection active | Boolean | 15425 | 17 | 315426.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_GFDI_protection_active
463 | Available | Input Register | U3 Fan fault | Boolean | 15425 | 18 | 315426.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Fan_fault
464 | Available | Input Register | U3 DC overcurrent | Boolean | 15425 | 21 | 315426.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_DC_overcurrent
465 | Available | Input Register | U3 AC overcurrent | Boolean | 15425 | 22 | 315426.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_AC_overcurrent
466 | Available | Input Register | U3 Frequency abnormal | Boolean | 15425 | 23 | 315426.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Frequency_abnormal
467 | Available | Input Register | U3 Temperature abnormal | Boolean | 15425 | 24 | 315426.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Temperature_abnormal
468 | Available | Input Register | U3 Hardware fault | Boolean | 15425 | 25 | 315426.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Hardware_fault
469 | Available | Input Register | U3 Grounding fault | Boolean | 15425 | 26 | 315426.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Grounding_fault
470 | Available | Input Register | U3 Bus overvoltage | Boolean | 15425 | 27 | 315426.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Bus_overvoltage
471 | Available | Input Register | U3 Bus undervoltage | Boolean | 15425 | 28 | 315426.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Bus_undervoltage
472 | Available | Input Register | U3 Inverter overvoltage | Boolean | 15425 | 29 | 315426.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15425_U3_Inverter_overvoltage
473 | Available | Input Register | U3 Fault State 2 | 32-bit bitfield | 15427 |  | 315428 | [14 empty] | IREG_15427_U3_Fault_State_2
474 | Available | Input Register | U3 Insulation impedance fault | Boolean | 15427 | 0 | 315428.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Insulation_impedance_fault
475 | Available | Input Register | U3 AC SPD fault | Boolean | 15427 | 1 | 315428.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_AC_SPD_fault
476 | Available | Input Register | U3 Sampling fault | Boolean | 15427 | 2 | 315428.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Sampling_fault
477 | Available | Input Register | U3 DC polarity reversed alarm | Boolean | 15427 | 3 | 315428.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_polarity_reversed_alarm
478 | Available | Input Register | U3 Control power supply fault | Boolean | 15427 | 4 | 315428.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Control_power_supply_fault
479 | Available | Input Register | U3 Backup power supply fault | Boolean | 15427 | 5 | 315428.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Backup_power_supply_fault
480 | Available | Input Register | U3 AC current imballance | Boolean | 15427 | 6 | 315428.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_AC_current_imballance
481 | Available | Input Register | U3 AC fuse fault | Boolean | 15427 | 7 | 315428.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_AC_fuse_fault
482 | Available | Input Register | U3 DC SPD fault | Boolean | 15427 | 8 | 315428.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_SPD_fault
483 | Available | Input Register | U3 Buffer contactor fault | Boolean | 15427 | 9 | 315428.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Buffer_contactor_fault
484 | Available | Input Register | U3 DC injection fault | Boolean | 15427 | 10 | 315428.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_injection_fault
485 | Available | Input Register | U3 DC switch fault | Boolean | 15427 | 11 | 315428.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_switch_fault
486 | Available | Input Register | U3 Device code repeat fault | Boolean | 15427 | 12 | 315428.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Device_code_repeat_fault
487 | Available | Input Register | U3 Parallel operation communication failure | Boolean | 15427 | 13 | 315428.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Parallel_operation_communication_failure
488 | Available | Input Register | U3 Control cabinet temperature alarm | Boolean | 15427 | 14 | 315428.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Control_cabinet_temperature_alarm
489 | Available | Input Register | U3 DC fuse grounding fault | Boolean | 15427 | 15 | 315428.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_fuse_grounding_fault
490 | Available | Input Register | U3 Reversed branch over current | Boolean | 15427 | 16 | 315428.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Reversed_branch_over_current
491 | Available | Input Register | U3 Grid voltage imballance | Boolean | 15427 | 17 | 315428.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Grid_voltage_imballance
492 | Available | Input Register | U3 inverter cabinet temperature alarm | Boolean | 15427 | 19 | 315428.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_inverter_cabinet_temperature_alarm
493 | Available | Input Register | U3 AC cabinet temperature alarm | Boolean | 15427 | 20 | 315428.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_AC_cabinet_temperature_alarm
494 | Available | Input Register | U3 AC switch disconnection | Boolean | 15427 | 21 | 315428.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_AC_switch_disconnection
495 | Available | Input Register | U3 AC switch fault | Boolean | 15427 | 22 | 315428.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_AC_switch_fault
496 | Available | Input Register | U3 Soft start fault | Boolean | 15427 | 23 | 315428.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Soft_start_fault
497 | Available | Input Register | U3 DC voltage sampling fault | Boolean | 15427 | 24 | 315428.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_voltage_sampling_fault
498 | Available | Input Register | U3 Fan 2 fault | Boolean | 15427 | 25 | 315428.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Fan_2_fault
499 | Available | Input Register | U3 Current unbalance 2 | Boolean | 15427 | 26 | 315428.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Current_unbalance_2
500 | Available | Input Register | U3 Current unbalance 3 | Boolean | 15427 | 27 | 315428.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Current_unbalance_3
501 | Available | Input Register | U3 DC cabinet temperature alarm | Boolean | 15427 | 29 | 315428.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_DC_cabinet_temperature_alarm
502 | Available | Input Register | U3 Neutral point potential shift alarm | Boolean | 15427 | 30 | 315428.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Neutral_point_potential_shift_alarm
503 | Available | Input Register | U3 Carrier sync failure | Boolean | 15427 | 31 | 315428.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15427_U3_Carrier_sync_failure
504 | Available | Input Register | U3 Fault State 3 | 32-bit bitfield | 15429 |  | 315430 | [14 empty] | IREG_15429_U3_Fault_State_3
505 | Available | Input Register | U3 smoke sensing fault | Boolean | 15429 | 0 | 315430.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15429_U3_smoke_sensing_fault
506 | Available | Input Register | U3 access control fault | Boolean | 15429 | 1 | 315430.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15429_U3_access_control_fault
507 | Available | Input Register | U3 Emergency fault shutdown fault | Boolean | 15429 | 2 | 315430.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15429_U3_Emergency_fault_shutdown_fault
508 | Available | Input Register | U3 Node State 1 | 32-bit bitfield | 15433 |  | 315434 | [14 empty] | IREG_15433_U3_Node_State_1
509 | Available | Input Register | U3 AC circuit breaker status | Boolean | 15433 | 0 | 315434.0 |  | None | Closed | Open | [10 empty] | IREG_15433_U3_AC_circuit_breaker_status
510 | Available | Input Register | U3 DC switch 1 status | Boolean | 15433 | 3 | 315434.3 |  | None | Closed | Open | [10 empty] | IREG_15433_U3_DC_switch_1_status
511 | Available | Input Register | U3 smoke node status | Boolean | 15433 | 17 | 315434.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15433_U3_smoke_node_status
512 | Available | Input Register | U3 access node status | Boolean | 15433 | 18 | 315434.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15433_U3_access_node_status
513 | Available | Input Register | U3 emergency shutdown status | Boolean | 15433 | 19 | 315434.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15433_U3_emergency_shutdown_status
514 | Available | Input Register | U3 Temperature 1 | 16-bit signed integer | 15437 |  | 315438 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15437_U3_Temperature_1_degC
515 | Available | Input Register | U3 Temperature 3 | 16-bit signed integer | 15439 |  | 315440 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15439_U3_Temperature_3_degC
516 | Available | Input Register | U3 Temperature 5 | 16-bit signed integer | 15441 |  | 315442 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15441_U3_Temperature_5_degC
517 | Available | Input Register | U3 Positive Resistance to Ground | 32-bit unsigned integer | 15443 |  | 315444 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15443_U3_Positive_Resistance_to_Ground_kOhm
518 | Available | Input Register | U3 Negative Resistance to Ground | 32-bit unsigned integer | 15445 |  | 315446 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15445_U3_Negative_Resistance_to_Ground_kOhm
519 | Available | Input Register | U3 Work State | 32-bit bitfield | 15447 |  | 315448 | [14 empty] | IREG_15447_U3_Work_State
520 | Available | Input Register | U3 Running | Boolean | 15447 | 0 | 315448.0 |  | None | Running | Not Running | [10 empty] | IREG_15447_U3_Running
521 | Available | Input Register | U3 Stopped | Boolean | 15447 | 1 | 315448.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15447_U3_Stopped
522 | Available | Input Register | U3 Initial Standby | Boolean | 15447 | 2 | 315448.2 |  | None | Standby | Not Standby | [10 empty] | IREG_15447_U3_Initial_Standby
523 | Available | Input Register | U3 Press to shutdown | Boolean | 15447 | 3 | 315448.3 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15447_U3_Press_to_shutdown
524 | Available | Input Register | U3 Standby | Boolean | 15447 | 4 | 315448.4 |  | None | Standby | Not Standby | [10 empty] | IREG_15447_U3_Standby
525 | Available | Input Register | U3 Emergency Stop | Boolean | 15447 | 5 | 315448.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15447_U3_Emergency_Stop
526 | Available | Input Register | U3 Starting | Boolean | 15447 | 6 | 315448.6 |  | None | Starting | Not Starting | [10 empty] | IREG_15447_U3_Starting
527 | Available | Input Register | U3 Stopping | Boolean | 15447 | 7 | 315448.7 |  | None | Stopping | Not Stopping | [10 empty] | IREG_15447_U3_Stopping
528 | Available | Input Register | U3 Fault Stop | Boolean | 15447 | 9 | 315448.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15447_U3_Fault_Stop
529 | Available | Input Register | U3 Alarm running | Boolean | 15447 | 10 | 315448.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15447_U3_Alarm_running
530 | Available | Input Register | U3 Derating running | Boolean | 15447 | 11 | 315448.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15447_U3_Derating_running
531 | Available | Input Register | U3 IO-DSP communication failure | Boolean | 15447 | 13 | 315448.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15447_U3_IO_DSP_communication_failure
532 | Available | Input Register | U3 Inverter is running | Boolean | 15447 | 17 | 315448.17 |  | None | Running | Not Running | [10 empty] | IREG_15447_U3_Inverter_is_running
533 | Available | Input Register | U3 Inverter is stopped | Boolean | 15447 | 18 | 315448.18 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15447_U3_Inverter_is_stopped
534 | Available | Input Register | U3 Anti-PID active | Boolean | 15447 | 19 | 315448.19 |  | On (1) | Active | Not-Active | [10 empty] | IREG_15447_U3_Anti_PID_active
535 | Available | Input Register | U3 Alarm State | 32-bit bitfield | 15449 |  | 315450 | [14 empty] | IREG_15449_U3_Alarm_State
536 | Available | Input Register | U3 Temperature alarm | Boolean | 15449 | 0 | 315450.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Temperature_alarm
537 | Available | Input Register | U3 Low insulation resistance alarm | Boolean | 15449 | 1 | 315450.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Low_insulation_resistance_alarm
538 | Available | Input Register | U3 GFRT operation alarm | Boolean | 15449 | 2 | 315450.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_GFRT_operation_alarm
539 | Available | Input Register | U3 CT unbalance | Boolean | 15449 | 3 | 315450.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_CT_unbalance
540 | Available | Input Register | U3 DC sensor fault | Boolean | 15449 | 6 | 315450.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_DC_sensor_fault
541 | Available | Input Register | U3 DC SPD fault | Boolean | 15449 | 7 | 315450.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_DC_SPD_fault
542 | Available | Input Register | U3 AC SPD fault | Boolean | 15449 | 8 | 315450.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_AC_SPD_fault
543 | Available | Input Register | U3 DC switch fault | Boolean | 15449 | 12 | 315450.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_DC_switch_fault
544 | Available | Input Register | U3 Anti-PID power supply | Boolean | 15449 | 13 | 315450.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Anti_PID_power_supply
545 | Available | Input Register | U3 Fan fault | Boolean | 15449 | 14 | 315450.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Fan_fault
546 | Available | Input Register | U3 DC bypass forward overcurrent alarm | Boolean | 15449 | 16 | 315450.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_DC_bypass_forward_overcurrent_alarm
547 | Available | Input Register | U3 DC bypass reverse overcurrent alarm | Boolean | 15449 | 17 | 315450.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_DC_bypass_reverse_overcurrent_alarm
548 | Available | Input Register | U3 AC circuit breaker fault | Boolean | 15449 | 19 | 315450.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_AC_circuit_breaker_fault
549 | Available | Input Register | U3 Meter communication failure | Boolean | 15449 | 20 | 315450.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Meter_communication_failure
550 | Available | Input Register | U3 Fan 2 fault | Boolean | 15449 | 21 | 315450.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Fan_2_fault
551 | Available | Input Register | U3 Temperature and humidity sensor fault | Boolean | 15449 | 23 | 315450.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Temperature_and_humidity_sensor_fault
552 | Available | Input Register | U3 Frequency deviation active power regulation | Boolean | 15449 | 24 | 315450.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Frequency_deviation_active_power_regulation
553 | Available | Input Register | U3 Voltage deviation reactive power regulation | Boolean | 15449 | 25 | 315450.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Voltage_deviation_reactive_power_regulation
554 | Available | Input Register | U3 Busbar temperature alarm | Boolean | 15449 | 27 | 315450.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Busbar_temperature_alarm
555 | Available | Input Register | U3 Abnormal derating of fan | Boolean | 15449 | 28 | 315450.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Abnormal_derating_of_fan
556 | Available | Input Register | U3 Frequency abnormal | Boolean | 15449 | 30 | 315450.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15449_U3_Frequency_abnormal
557 | Available | Input Register | U3 Negative Voltage to Ground | 16-bit signed integer | 15451 |  | 315452 |  |  |  |  | V | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15451_U3_Negative_Voltage_to_Ground_V
558 | Available | Input Register | U3 Annual Power Yield | 32-bit unsigned integer | 15452 |  | 315453 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15452_U3_Annual_Power_Yield_kWh |  | This point is not mapped to ignition
559 | Available | Input Register | U3 CO2 Emission Reduction | 32-bit unsigned integer | 15454 |  | 315455 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15454_U3_CO2_Emission_Reduction_kg |  | This point is not mapped to ignition
560 | Available | Input Register | U3 leakage current | 16-bit unsigned integer | 15484 |  | 315485 |  |  |  |  | A | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15484_U3_leakage_current_A
561 | Available | Input Register | U3 DC Input #1 | 16-bit signed integer | 15489 |  | 315490 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15489_U3_DC_Input_1_A
562 | Available | Input Register | U3 DC Input #2 | 16-bit signed integer | 15490 |  | 315491 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15490_U3_DC_Input_2_A
563 | Available | Input Register | U3 DC Input #3 | 16-bit signed integer | 15491 |  | 315492 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15491_U3_DC_Input_3_A
564 | Available | Input Register | U3 DC Input #4 | 16-bit signed integer | 15492 |  | 315493 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15492_U3_DC_Input_4_A
565 | Available | Input Register | U3 DC Input #5 | 16-bit signed integer | 15493 |  | 315494 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15493_U3_DC_Input_5_A
566 | Available | Input Register | U3 DC Input #6 | 16-bit signed integer | 15494 |  | 315495 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15494_U3_DC_Input_6_A
567 | Available | Input Register | U3 DC Input #7 | 16-bit signed integer | 15495 |  | 315496 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15495_U3_DC_Input_7_A
568 | Available | Input Register | U3 running status | 16-bit bitfield | 15501 |  | 315502 | [14 empty] | IREG_15501_U3_running_status
569 | Available | Input Register | U3 HVRT operation | Boolean | 15501 | 1 | 315502.1 |  | None | On | Off | [10 empty] | IREG_15501_U3_HVRT_operation
570 | Available | Input Register | U3 LVRT operation | Boolean | 15501 | 2 | 315502.2 |  | None | On | Off | [10 empty] | IREG_15501_U3_LVRT_operation
571 | Available | Input Register | U4 Daily power yield | 32-bit unsigned integer | 15509 |  | 315510 |  |  |  |  | kWh | 10 | 0 | 4294967295 | 0 | 429496729.5 |  |  |  |  | IREG_15509_U4_Daily_power_yield_kWh
572 | Available | Input Register | U4 Monthly power yield | 32-bit unsigned integer | 15511 |  | 315512 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15511_U4_Monthly_power_yield_kWh |  | This point is not mapped to ignition
573 | Available | Input Register | U4 Total power yield | 32-bit unsigned integer | 15513 |  | 315514 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15513_U4_Total_power_yield_kWh
574 | Available | Input Register | U4 Daily grid connected minutes | 16-bit unsigned integer | 15515 |  | 315516 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15515_U4_Daily_grid_connected_minutes_min
575 | Available | Input Register | U4 Total running hours | 32-bit unsigned integer | 15516 |  | 315517 |  |  |  |  | hr | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15516_U4_Total_running_hours_hr
576 | Available | Input Register | U4 Internal Module Temperature | 16-bit signed integer | 15518 |  | 315519 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15518_U4_Internal_Module_Temperature_degC
577 | Available | Input Register | U4 DC Voltage | 16-bit unsigned integer | 15519 |  | 315520 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15519_U4_DC_Voltage_V
578 | Available | Input Register | U4 DC Current | 16-bit unsigned integer | 15520 |  | 315521 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15520_U4_DC_Current_A
579 | Available | Input Register | U4 DC Power | 32-bit signed integer | 15521 |  | 315522 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15521_U4_DC_Power_W
580 | Available | Input Register | U4 Voltage A-B | 16-bit unsigned integer | 15523 |  | 315524 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15523_U4_Voltage_A_B_V
581 | Available | Input Register | U4 Voltage B-C | 16-bit unsigned integer | 15524 |  | 315525 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15524_U4_Voltage_B_C_V
582 | Available | Input Register | U4 Voltage C-A | 16-bit unsigned integer | 15525 |  | 315526 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15525_U4_Voltage_C_A_V
583 | Available | Input Register | U4 Phase A Current | 16-bit unsigned integer | 15526 |  | 315527 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15526_U4_Phase_A_Current_A
584 | Available | Input Register | U4 Phase B Current | 16-bit unsigned integer | 15527 |  | 315528 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15527_U4_Phase_B_Current_A
585 | Available | Input Register | U4 Phase C Current | 16-bit unsigned integer | 15528 |  | 315529 |  |  |  |  | A | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15528_U4_Phase_C_Current_A
586 | Available | Input Register | U4 Active Power | 32-bit signed integer | 15529 |  | 315530 |  |  |  |  | W | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15529_U4_Active_Power_W
587 | Available | Input Register | U4 Reactive Power | 32-bit signed integer | 15531 |  | 315532 |  |  |  |  | var | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  |  |  | IREG_15531_U4_Reactive_Power_var
588 | Available | Input Register | U4 Power Factor | 16-bit signed integer | 15533 |  | 315534 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | IREG_15533_U4_Power_Factor_PU
589 | Available | Input Register | U4 Frequency | 16-bit unsigned integer | 15534 |  | 315535 |  |  |  |  | Hz | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15534_U4_Frequency_Hz
590 | Available | Input Register | U4 Efficiency | 16-bit unsigned integer | 15535 |  | 315536 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15535_U4_Efficiency_pct
591 | Available | Input Register | U4 Clock Year | 16-bit unsigned integer | 15537 |  | 315538 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15537_U4_Clock_Year_year |  | This point is not mapped to ignition
592 | Available | Input Register | U4 Clock Month | 16-bit unsigned integer | 15538 |  | 315539 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15538_U4_Clock_Month_month |  | This point is not mapped to ignition
593 | Available | Input Register | U4 Clock Day | 16-bit unsigned integer | 15539 |  | 315540 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15539_U4_Clock_Day_day |  | This point is not mapped to ignition
594 | Available | Input Register | U4 Clock Hour | 16-bit unsigned integer | 15540 |  | 315541 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15540_U4_Clock_Hour_hr |  | This point is not mapped to ignition
595 | Available | Input Register | U4 Clock Minute | 16-bit unsigned integer | 15541 |  | 315542 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15541_U4_Clock_Minute_min |  | This point is not mapped to ignition
596 | Available | Input Register | U4 Clock Second | 16-bit unsigned integer | 15542 |  | 315543 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15542_U4_Clock_Second_s |  | This point is not mapped to ignition
597 | Available | Input Register | U4 Fault State 1 | 32-bit bitfield | 15545 |  | 315546 | [14 empty] | IREG_15545_U4_Fault_State_1
598 | Available | Input Register | U4 DC undervoltage alarm | Boolean | 15545 | 0 | 315546.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_DC_undervoltage_alarm
599 | Available | Input Register | U4 DC overvoltage alarm | Boolean | 15545 | 1 | 315546.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_DC_overvoltage_alarm
600 | Available | Input Register | U4 AC undervoltage alarm | Boolean | 15545 | 2 | 315546.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_AC_undervoltage_alarm
601 | Available | Input Register | U4 AC overvoltage alarm | Boolean | 15545 | 3 | 315546.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_AC_overvoltage_alarm
602 | Available | Input Register | U4 Anti islanding protection active | Boolean | 15545 | 7 | 315546.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Anti_islanding_protection_active
603 | Available | Input Register | U4 PDP protection active | Boolean | 15545 | 9 | 315546.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_PDP_protection_active
604 | Available | Input Register | U4 Module overtemperature alarm | Boolean | 15545 | 10 | 315546.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Module_overtemperature_alarm
605 | Available | Input Register | U4 Reactor overtemperature alarm | Boolean | 15545 | 11 | 315546.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Reactor_overtemperature_alarm
606 | Available | Input Register | U4 AC leakage current protection alarm | Boolean | 15545 | 14 | 315546.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_AC_leakage_current_protection_alarm
607 | Available | Input Register | U4 GFDI protection active | Boolean | 15545 | 17 | 315546.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_GFDI_protection_active
608 | Available | Input Register | U4 Fan fault | Boolean | 15545 | 18 | 315546.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Fan_fault
609 | Available | Input Register | U4 DC overcurrent | Boolean | 15545 | 21 | 315546.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_DC_overcurrent
610 | Available | Input Register | U4 AC overcurrent | Boolean | 15545 | 22 | 315546.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_AC_overcurrent
611 | Available | Input Register | U4 Frequency abnormal | Boolean | 15545 | 23 | 315546.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Frequency_abnormal
612 | Available | Input Register | U4 Temperature abnormal | Boolean | 15545 | 24 | 315546.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Temperature_abnormal
613 | Available | Input Register | U4 Hardware fault | Boolean | 15545 | 25 | 315546.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Hardware_fault
614 | Available | Input Register | U4 Grounding fault | Boolean | 15545 | 26 | 315546.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Grounding_fault
615 | Available | Input Register | U4 Bus overvoltage | Boolean | 15545 | 27 | 315546.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Bus_overvoltage
616 | Available | Input Register | U4 Bus undervoltage | Boolean | 15545 | 28 | 315546.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Bus_undervoltage
617 | Available | Input Register | U4 Inverter overvoltage | Boolean | 15545 | 29 | 315546.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15545_U4_Inverter_overvoltage
618 | Available | Input Register | U4 Fault State 2 | 32-bit bitfield | 15547 |  | 315548 | [14 empty] | IREG_15547_U4_Fault_State_2
619 | Available | Input Register | U4 Insulation impedance fault | Boolean | 15547 | 0 | 315548.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Insulation_impedance_fault
620 | Available | Input Register | U4 AC SPD fault | Boolean | 15547 | 1 | 315548.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_AC_SPD_fault
621 | Available | Input Register | U4 Sampling fault | Boolean | 15547 | 2 | 315548.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Sampling_fault
622 | Available | Input Register | U4 DC polarity reversed alarm | Boolean | 15547 | 3 | 315548.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_polarity_reversed_alarm
623 | Available | Input Register | U4 Control power supply fault | Boolean | 15547 | 4 | 315548.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Control_power_supply_fault
624 | Available | Input Register | U4 Backup power supply fault | Boolean | 15547 | 5 | 315548.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Backup_power_supply_fault
625 | Available | Input Register | U4 AC current imballance | Boolean | 15547 | 6 | 315548.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_AC_current_imballance
626 | Available | Input Register | U4 AC fuse fault | Boolean | 15547 | 7 | 315548.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_AC_fuse_fault
627 | Available | Input Register | U4 DC SPD fault | Boolean | 15547 | 8 | 315548.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_SPD_fault
628 | Available | Input Register | U4 Buffer contactor fault | Boolean | 15547 | 9 | 315548.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Buffer_contactor_fault
629 | Available | Input Register | U4 DC injection fault | Boolean | 15547 | 10 | 315548.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_injection_fault
630 | Available | Input Register | U4 DC switch fault | Boolean | 15547 | 11 | 315548.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_switch_fault
631 | Available | Input Register | U4 Device code repeat fault | Boolean | 15547 | 12 | 315548.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Device_code_repeat_fault
632 | Available | Input Register | U4 Parallel operation communication failure | Boolean | 15547 | 13 | 315548.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Parallel_operation_communication_failure
633 | Available | Input Register | U4 Control cabinet temperature alarm | Boolean | 15547 | 14 | 315548.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Control_cabinet_temperature_alarm
634 | Available | Input Register | U4 DC fuse grounding fault | Boolean | 15547 | 15 | 315548.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_fuse_grounding_fault
635 | Available | Input Register | U4 Reversed branch over current | Boolean | 15547 | 16 | 315548.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Reversed_branch_over_current
636 | Available | Input Register | U4 Grid voltage imballance | Boolean | 15547 | 17 | 315548.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Grid_voltage_imballance
637 | Available | Input Register | U4 inverter cabinet temperature alarm | Boolean | 15547 | 19 | 315548.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_inverter_cabinet_temperature_alarm
638 | Available | Input Register | U4 AC cabinet temperature alarm | Boolean | 15547 | 20 | 315548.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_AC_cabinet_temperature_alarm
639 | Available | Input Register | U4 AC switch disconnection | Boolean | 15547 | 21 | 315548.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_AC_switch_disconnection
640 | Available | Input Register | U4 AC switch fault | Boolean | 15547 | 22 | 315548.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_AC_switch_fault
641 | Available | Input Register | U4 Soft start fault | Boolean | 15547 | 23 | 315548.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Soft_start_fault
642 | Available | Input Register | U4 DC voltage sampling fault | Boolean | 15547 | 24 | 315548.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_voltage_sampling_fault
643 | Available | Input Register | U4 Fan 2 fault | Boolean | 15547 | 25 | 315548.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Fan_2_fault
644 | Available | Input Register | U4 Current unbalance 2 | Boolean | 15547 | 26 | 315548.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Current_unbalance_2
645 | Available | Input Register | U4 Current unbalance 3 | Boolean | 15547 | 27 | 315548.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Current_unbalance_3
646 | Available | Input Register | U4 DC cabinet temperature alarm | Boolean | 15547 | 29 | 315548.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_DC_cabinet_temperature_alarm
647 | Available | Input Register | U4 Neutral point potential shift alarm | Boolean | 15547 | 30 | 315548.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Neutral_point_potential_shift_alarm
648 | Available | Input Register | U4 Carrier sync failure | Boolean | 15547 | 31 | 315548.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15547_U4_Carrier_sync_failure
649 | Available | Input Register | U4 Fault State 3 | 32-bit bitfield | 15549 |  | 315550 | [14 empty] | IREG_15549_U4_Fault_State_3
650 | Available | Input Register | U4 smoke sensing fault | Boolean | 15549 | 0 | 315550.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15549_U4_smoke_sensing_fault
651 | Available | Input Register | U4 access control fault | Boolean | 15549 | 1 | 315550.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15549_U4_access_control_fault
652 | Available | Input Register | U4 Emergency fault shutdown fault | Boolean | 15549 | 2 | 315550.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15549_U4_Emergency_fault_shutdown_fault
653 | Available | Input Register | U4 Node State 1 | 32-bit bitfield | 15553 |  | 315554 | [14 empty] | IREG_15553_U4_Node_State_1
654 | Available | Input Register | U4 AC circuit breaker status | Boolean | 15553 | 0 | 315554.0 |  | None | Closed | Open | [10 empty] | IREG_15553_U4_AC_circuit_breaker_status
655 | Available | Input Register | U4 DC switch 1 status | Boolean | 15553 | 3 | 315554.3 |  | None | Closed | Open | [10 empty] | IREG_15553_U4_DC_switch_1_status
656 | Available | Input Register | U4 smoke node status | Boolean | 15553 | 17 | 315554.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15553_U4_smoke_node_status
657 | Available | Input Register | U4 access node status | Boolean | 15553 | 18 | 315554.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15553_U4_access_node_status
658 | Available | Input Register | U4 emergency shutdown status | Boolean | 15553 | 19 | 315554.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15553_U4_emergency_shutdown_status
659 | Available | Input Register | U4 Temperature 1 | 16-bit signed integer | 15557 |  | 315558 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15557_U4_Temperature_1_degC
660 | Available | Input Register | U4 Temperature 3 | 16-bit signed integer | 15559 |  | 315560 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15559_U4_Temperature_3_degC
661 | Available | Input Register | U4 Temperature 5 | 16-bit signed integer | 15561 |  | 315562 |  |  |  |  | degC | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15561_U4_Temperature_5_degC
662 | Available | Input Register | U4 Positive Resistance to Ground | 32-bit unsigned integer | 15563 |  | 315564 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15563_U4_Positive_Resistance_to_Ground_kOhm
663 | Available | Input Register | U4 Negative Resistance to Ground | 32-bit unsigned integer | 15565 |  | 315566 |  |  |  |  | kOhm | 100 | 0 | 4294967295 | 0 | 42949672.95 |  |  |  |  | IREG_15565_U4_Negative_Resistance_to_Ground_kOhm
664 | Available | Input Register | U4 Work State | 32-bit bitfield | 15567 |  | 315568 | [14 empty] | IREG_15567_U4_Work_State
665 | Available | Input Register | U4 Running | Boolean | 15567 | 0 | 315568.0 |  | None | Running | Not Running | [10 empty] | IREG_15567_U4_Running
666 | Available | Input Register | U4 Stopped | Boolean | 15567 | 1 | 315568.1 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15567_U4_Stopped
667 | Available | Input Register | U4 Initial Standby | Boolean | 15567 | 2 | 315568.2 |  | None | Standby | Not Standby | [10 empty] | IREG_15567_U4_Initial_Standby
668 | Available | Input Register | U4 Press to shutdown | Boolean | 15567 | 3 | 315568.3 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15567_U4_Press_to_shutdown
669 | Available | Input Register | U4 Standby | Boolean | 15567 | 4 | 315568.4 |  | None | Standby | Not Standby | [10 empty] | IREG_15567_U4_Standby
670 | Available | Input Register | U4 Emergency Stop | Boolean | 15567 | 5 | 315568.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15567_U4_Emergency_Stop
671 | Available | Input Register | U4 Starting | Boolean | 15567 | 6 | 315568.6 |  | None | Starting | Not Starting | [10 empty] | IREG_15567_U4_Starting
672 | Available | Input Register | U4 Stopping | Boolean | 15567 | 7 | 315568.7 |  | None | Stopping | Not Stopping | [10 empty] | IREG_15567_U4_Stopping
673 | Available | Input Register | U4 Fault Stop | Boolean | 15567 | 9 | 315568.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15567_U4_Fault_Stop
674 | Available | Input Register | U4 Alarm running | Boolean | 15567 | 10 | 315568.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15567_U4_Alarm_running
675 | Available | Input Register | U4 Derating running | Boolean | 15567 | 11 | 315568.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15567_U4_Derating_running
676 | Available | Input Register | U4 IO-DSP communication failure | Boolean | 15567 | 13 | 315568.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15567_U4_IO_DSP_communication_failure
677 | Available | Input Register | U4 Inverter is running | Boolean | 15567 | 17 | 315568.17 |  | None | Running | Not Running | [10 empty] | IREG_15567_U4_Inverter_is_running
678 | Available | Input Register | U4 Inverter is stopped | Boolean | 15567 | 18 | 315568.18 |  | None | Stopped | Not Stopped | [10 empty] | IREG_15567_U4_Inverter_is_stopped
679 | Available | Input Register | U4 Anti-PID active | Boolean | 15567 | 19 | 315568.19 |  | On (1) | Active | Not-Active | [10 empty] | IREG_15567_U4_Anti_PID_active
680 | Available | Input Register | U4 Alarm State | 32-bit bitfield | 15569 |  | 315570 | [14 empty] | IREG_15569_U4_Alarm_State
681 | Available | Input Register | U4 Temperature alarm | Boolean | 15569 | 0 | 315570.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Temperature_alarm
682 | Available | Input Register | U4 Low insulation resistance alarm | Boolean | 15569 | 1 | 315570.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Low_insulation_resistance_alarm
683 | Available | Input Register | U4 GFRT operation alarm | Boolean | 15569 | 2 | 315570.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_GFRT_operation_alarm
684 | Available | Input Register | U4 CT unbalance | Boolean | 15569 | 3 | 315570.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_CT_unbalance
685 | Available | Input Register | U4 DC sensor fault | Boolean | 15569 | 6 | 315570.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_DC_sensor_fault
686 | Available | Input Register | U4 DC SPD fault | Boolean | 15569 | 7 | 315570.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_DC_SPD_fault
687 | Available | Input Register | U4 AC SPD fault | Boolean | 15569 | 8 | 315570.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_AC_SPD_fault
688 | Available | Input Register | U4 DC switch fault | Boolean | 15569 | 12 | 315570.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_DC_switch_fault
689 | Available | Input Register | U4 Anti-PID power supply | Boolean | 15569 | 13 | 315570.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Anti_PID_power_supply
690 | Available | Input Register | U4 Fan fault | Boolean | 15569 | 14 | 315570.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Fan_fault
691 | Available | Input Register | U4 DC bypass forward overcurrent alarm | Boolean | 15569 | 16 | 315570.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_DC_bypass_forward_overcurrent_alarm
692 | Available | Input Register | U4 DC bypass reverse overcurrent alarm | Boolean | 15569 | 17 | 315570.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_DC_bypass_reverse_overcurrent_alarm
693 | Available | Input Register | U4 AC circuit breaker fault | Boolean | 15569 | 19 | 315570.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_AC_circuit_breaker_fault
694 | Available | Input Register | U4 Meter communication failure | Boolean | 15569 | 20 | 315570.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Meter_communication_failure
695 | Available | Input Register | U4 Fan 2 fault | Boolean | 15569 | 21 | 315570.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Fan_2_fault
696 | Available | Input Register | U4 Temperature and humidity sensor fault | Boolean | 15569 | 23 | 315570.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Temperature_and_humidity_sensor_fault
697 | Available | Input Register | U4 Frequency deviation active power regulation | Boolean | 15569 | 24 | 315570.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Frequency_deviation_active_power_regulation
698 | Available | Input Register | U4 Voltage deviation reactive power regulation | Boolean | 15569 | 25 | 315570.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Voltage_deviation_reactive_power_regulation
699 | Available | Input Register | U4 Busbar temperature alarm | Boolean | 15569 | 27 | 315570.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Busbar_temperature_alarm
700 | Available | Input Register | U4 Abnormal derating of fan | Boolean | 15569 | 28 | 315570.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Abnormal_derating_of_fan
701 | Available | Input Register | U4 Frequency abnormal | Boolean | 15569 | 30 | 315570.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15569_U4_Frequency_abnormal
702 | Available | Input Register | U4 Negative Voltage to Ground | 16-bit signed integer | 15571 |  | 315572 |  |  |  |  | V | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15571_U4_Negative_Voltage_to_Ground_V
703 | Available | Input Register | U4 Annual Power Yield | 32-bit unsigned integer | 15572 |  | 315573 |  |  |  |  | kWh | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15572_U4_Annual_Power_Yield_kWh |  | This point is not mapped to ignition
704 | Available | Input Register | U4 CO2 Emission Reduction | 32-bit unsigned integer | 15574 |  | 315575 |  |  |  |  | kg | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  |  |  | IREG_15574_U4_CO2_Emission_Reduction_kg |  | This point is not mapped to ignition
705 | Available | Input Register | U4 leakage current | 16-bit unsigned integer | 15604 |  | 315605 |  |  |  |  | A | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15604_U4_leakage_current_A
706 | Available | Input Register | U4 DC Input #1 | 16-bit signed integer | 15609 |  | 315610 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15609_U4_DC_Input_1_A
707 | Available | Input Register | U4 DC Input #2 | 16-bit signed integer | 15610 |  | 315611 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15610_U4_DC_Input_2_A
708 | Available | Input Register | U4 DC Input #3 | 16-bit signed integer | 15611 |  | 315612 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15611_U4_DC_Input_3_A
709 | Available | Input Register | U4 DC Input #4 | 16-bit signed integer | 15612 |  | 315613 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15612_U4_DC_Input_4_A
710 | Available | Input Register | U4 DC Input #5 | 16-bit signed integer | 15613 |  | 315614 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15613_U4_DC_Input_5_A
711 | Available | Input Register | U4 DC Input #6 | 16-bit signed integer | 15614 |  | 315615 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15614_U4_DC_Input_6_A
712 | Available | Input Register | U4 DC Input #7 | 16-bit signed integer | 15615 |  | 315616 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15615_U4_DC_Input_7_A
713 | Available | Input Register | U4 running status | 16-bit bitfield | 15621 |  | 315622 | [14 empty] | IREG_15621_U4_running_status
714 | Available | Input Register | U4 HVRT operation | Boolean | 15621 | 1 | 315622.1 |  | None | On | Off | [10 empty] | IREG_15621_U4_HVRT_operation
715 | Available | Input Register | U4 LVRT operation | Boolean | 15621 | 2 | 315622.2 |  | None | On | Off | [10 empty] | IREG_15621_U4_LVRT_operation
716 | Available | Input Register | ISO board fault status | 16-bit bitfield | 15629 |  | 315630 | [14 empty] | IREG_15629_ISO_board_fault_status
717 | Available | Input Register | ISO insulation detection abnormal | Boolean | 15629 | 0 | 315630.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15629_ISO_insulation_detection_abnormal
718 | Available | Input Register | ISO hardware fault | Boolean | 15629 | 3 | 315630.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15629_ISO_hardware_fault
719 | Available | Input Register | ISO overtemperature fault | Boolean | 15629 | 4 | 315630.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15629_ISO_overtemperature_fault
720 | Available | Input Register | ISO overvoltage fault | Boolean | 15629 | 5 | 315630.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15629_ISO_overvoltage_fault
721 | Available | Input Register | ISO board alarm status | 16-bit bitfield | 15630 |  | 315631 | [14 empty] | IREG_15630_ISO_board_alarm_status
722 | Available | Input Register | ISO insulation detection abnormal | Boolean | 15630 | 0 | 315631.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15630_ISO_insulation_detection_abnormal
723 | Available | Input Register | ISO overtemperature alarm | Boolean | 15630 | 3 | 315631.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15630_ISO_overtemperature_alarm
724 | Available | Input Register | ISO grid sampling abonormal | Boolean | 15630 | 4 | 315631.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_15630_ISO_grid_sampling_abonormal
725 | Available | Input Register | 24h insulation resistance | 16-bit unsigned integer | 15631 |  | 315632 |  |  |  |  | kΩ | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_15631_24h_insulation_resistance_kΩ
726 | Available | Input Register | Certified Software Version | String | 15633 |  | 315634 | [14 empty] | IREG_15633_Certified_Software_Version |  | This point is not mapped to ignition
727 | Available | Input Register | Overexcitation Specified Active Power | 32-bit signed integer | 15698 |  | 315699 |  |  |  |  | kW | 10 | -2147483648 | 2147483647 | -214748364.8 | 214748364.7 |  |  |  |  | IREG_15698_Overexcitation_Specified_Active_Power_kW |  | This point is not mapped to ignition
728 | Available | Input Register | Underexcitation Specified Active Power | 32-bit signed integer | 15700 |  | 315701 |  |  |  |  | kW | 10 | -2147483648 | 2147483647 | -214748364.8 | 214748364.7 |  |  |  |  | IREG_15700_Underexcitation_Specified_Active_Power_kW |  | This point is not mapped to ignition
729 | Available | Input Register | Commercial Plant Running Status | 16-bit unsigned integer | 15702 |  | 315703 |  | Off (0) | Running | Offline | boolean |  | 0 | 65535 | [6 empty] | IREG_15702_Commercial_Plant_Running_Status_boolean |  | This point is not mapped to ignition
730 | Not Available | Input Register | Maximum Appearant Power | 16-bit unsigned integer | 15703 |  | 315704 |  |  |  |  | kVA | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15703_Maximum_Appearant_Power_kVA
731 | Not Available | Input Register | Maximum Discharging Power | 16-bit unsigned integer | 15704 |  | 315705 |  |  |  |  | kW | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15704_Maximum_Discharging_Power_kW |  | This point is not mapped to ignition
732 | Not Available | Input Register | Maximum inductive reactive power | 16-bit signed integer | 15705 |  | 315706 |  |  |  |  | kvar | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15705_Maximum_inductive_reactive_power_kvar
733 | Not Available | Input Register | Maximum capacitive reactive power | 16-bit signed integer | 15706 |  | 315707 |  |  |  |  | kvar | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15706_Maximum_capacitive_reactive_power_kvar
734 | Available | Input Register | Grid connected status of commercial plant | 16-bit unsigned integer | 15707 |  | 315708 |  | Off (0) | Connected | Disconnected | boolean |  | 0 | 65535 | [6 empty] | IREG_15707_Grid_connected_status_of_commercial_plant_boolean |  | This point is not mapped to ignition
735 | Available | Input Register | Nominal AC voltage | 16-bit unsigned integer | 15708 |  | 315709 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15708_Nominal_AC_voltage_V |  | This point is not mapped to ignition
736 | Available | Input Register | Max AC Voltage | 16-bit unsigned integer | 15709 |  | 315710 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15709_Max_AC_Voltage_V |  | This point is not mapped to ignition
737 | Available | Input Register | Min AC Voltage | 16-bit unsigned integer | 15710 |  | 315711 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15710_Min_AC_Voltage_V |  | This point is not mapped to ignition
738 | Available | Input Register | QU Reference Voltage Current Value | 16-bit unsigned integer | 15732 |  | 315733 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | IREG_15732_QU_Reference_Voltage_Current_Value_V |  | This point is not mapped to ignition
739 | Available | Input Register | U1 Valid Recorder Quantity | 16-bit unsigned integer | 15733 |  | 315734 |  |  |  |  | count |  | 0 | 65535 | [6 empty] | IREG_15733_U1_Valid_Recorder_Quantity_count
740 | Available | Input Register | U2 Valid Recorder Quantity | 16-bit unsigned integer | 15734 |  | 315735 |  |  |  |  | count |  | 0 | 65535 | [6 empty] | IREG_15734_U2_Valid_Recorder_Quantity_count
741 | Available | Input Register | U3 Valid Recorder Quantity | 16-bit unsigned integer | 15735 |  | 315736 |  |  |  |  | count |  | 0 | 65535 | [6 empty] | IREG_15735_U3_Valid_Recorder_Quantity_count
742 | Available | Input Register | U4 Valid Recorder Quantity | 16-bit unsigned integer | 15736 |  | 315737 |  |  |  |  | count |  | 0 | 65535 | [6 empty] | IREG_15736_U4_Valid_Recorder_Quantity_count
743 | Not Available | Input Register | High side AB voltage | 16-bit unsigned integer | 15744 |  | 315745 |  |  |  |  | kV | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15744_High_side_AB_voltage_kV
744 | Not Available | Input Register | High side BC voltage | 16-bit unsigned integer | 15745 |  | 315746 |  |  |  |  | kV | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15745_High_side_BC_voltage_kV
745 | Not Available | Input Register | High side CA voltage | 16-bit unsigned integer | 15746 |  | 315747 |  |  |  |  | kV | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | IREG_15746_High_side_CA_voltage_kV
746 | Not Available | Input Register | High side active power | 32-bit signed integer | 15747 |  | 315748 |  |  |  |  | kW | 100 | -2147483648 | 2147483647 | -21474836.48 | 21474836.47 |  |  |  |  | IREG_15747_High_side_active_power_kW
747 | Not Available | Input Register | High side phase A current | 16-bit signed integer | 15749 |  | 315750 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15749_High_side_phase_A_current_A
748 | Not Available | Input Register | High side phase B current | 16-bit signed integer | 15750 |  | 315751 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15750_High_side_phase_B_current_A
749 | Not Available | Input Register | High side phase C current | 16-bit signed integer | 15751 |  | 315752 |  |  |  |  | A | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | IREG_15751_High_side_phase_C_current_A
750 | Not Available | Input Register | High side reactive power | 32-bit signed integer | 15753 |  | 315754 |  |  |  |  | kvar | 100 | -2147483648 | 2147483647 | -21474836.48 | 21474836.47 |  |  |  |  | IREG_15753_High_side_reactive_power_kvar
751 | Available | Input Register | Zone Monitor Work State | Enumeration | 15999 |  | 316000 | [14 empty] | IREG_15999_Zone_Monitor_Work_State | 0 to 2
752 | Available | Input Register | Branch Open Circuit Alarm | 32-bit bitfield | 16000 |  | 316001 | [14 empty] | IREG_16000_Branch_Open_Circuit_Alarm
753 | Available | Input Register | U1 open circuit fault branch 1 | Boolean | 16000 | 0 | 316001.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_1
754 | Available | Input Register | U1 open circuit fault branch 2 | Boolean | 16000 | 1 | 316001.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_2
755 | Available | Input Register | U1 open circuit fault branch 3 | Boolean | 16000 | 2 | 316001.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_3
756 | Available | Input Register | U1 open circuit fault branch 4 | Boolean | 16000 | 3 | 316001.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_4
757 | Available | Input Register | U1 open circuit fault branch 5 | Boolean | 16000 | 4 | 316001.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_5
758 | Available | Input Register | U1 open circuit fault branch 6 | Boolean | 16000 | 5 | 316001.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_6
759 | Available | Input Register | U1 open circuit fault branch 7 | Boolean | 16000 | 6 | 316001.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_7
760 | Available | Input Register | U1 open circuit fault branch 8 | Boolean | 16000 | 7 | 316001.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U1_open_circuit_fault_branch_8
761 | Available | Input Register | U2 open circuit fault branch 1 | Boolean | 16000 | 8 | 316001.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_1
762 | Available | Input Register | U2 open circuit fault branch 2 | Boolean | 16000 | 9 | 316001.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_2
763 | Available | Input Register | U2 open circuit fault branch 3 | Boolean | 16000 | 10 | 316001.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_3
764 | Available | Input Register | U2 open circuit fault branch 4 | Boolean | 16000 | 11 | 316001.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_4
765 | Available | Input Register | U2 open circuit fault branch 5 | Boolean | 16000 | 12 | 316001.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_5
766 | Available | Input Register | U2 open circuit fault branch 6 | Boolean | 16000 | 13 | 316001.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_6
767 | Available | Input Register | U2 open circuit fault branch 7 | Boolean | 16000 | 14 | 316001.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_7
768 | Available | Input Register | U2 open circuit fault branch 8 | Boolean | 16000 | 15 | 316001.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U2_open_circuit_fault_branch_8
769 | Available | Input Register | U3 open circuit fault branch 1 | Boolean | 16000 | 16 | 316001.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_1
770 | Available | Input Register | U3 open circuit fault branch 2 | Boolean | 16000 | 17 | 316001.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_2
771 | Available | Input Register | U3 open circuit fault branch 3 | Boolean | 16000 | 18 | 316001.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_3
772 | Available | Input Register | U3 open circuit fault branch 4 | Boolean | 16000 | 19 | 316001.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_4
773 | Available | Input Register | U3 open circuit fault branch 5 | Boolean | 16000 | 20 | 316001.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_5
774 | Available | Input Register | U3 open circuit fault branch 6 | Boolean | 16000 | 21 | 316001.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_6
775 | Available | Input Register | U3 open circuit fault branch 7 | Boolean | 16000 | 22 | 316001.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_7
776 | Available | Input Register | U3 open circuit fault branch 8 | Boolean | 16000 | 23 | 316001.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U3_open_circuit_fault_branch_8
777 | Available | Input Register | U4 open circuit fault branch 1 | Boolean | 16000 | 24 | 316001.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_1
778 | Available | Input Register | U4 open circuit fault branch 2 | Boolean | 16000 | 25 | 316001.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_2
779 | Available | Input Register | U4 open circuit fault branch 3 | Boolean | 16000 | 26 | 316001.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_3
780 | Available | Input Register | U4 open circuit fault branch 4 | Boolean | 16000 | 27 | 316001.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_4
781 | Available | Input Register | U4 open circuit fault branch 5 | Boolean | 16000 | 28 | 316001.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_5
782 | Available | Input Register | U4 open circuit fault branch 6 | Boolean | 16000 | 29 | 316001.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_6
783 | Available | Input Register | U4 open circuit fault branch 7 | Boolean | 16000 | 30 | 316001.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_7
784 | Available | Input Register | U4 open circuit fault branch 8 | Boolean | 16000 | 31 | 316001.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16000_U4_open_circuit_fault_branch_8
785 | Available | Input Register | Branch String Alarm | 32-bit bitfield | 16002 |  | 316003 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_Branch_String_Alarm
786 | Available | Input Register | U1 string failure branch 1 | Boolean | 16002 | 0 | 316003.0 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_1
787 | Available | Input Register | U1 string failure branch 2 | Boolean | 16002 | 1 | 316003.1 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_2
788 | Available | Input Register | U1 string failure branch 3 | Boolean | 16002 | 2 | 316003.2 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_3
789 | Available | Input Register | U1 string failure branch 4 | Boolean | 16002 | 3 | 316003.3 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_4
790 | Available | Input Register | U1 string failure branch 5 | Boolean | 16002 | 4 | 316003.4 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_5
791 | Available | Input Register | U1 string failure branch 6 | Boolean | 16002 | 5 | 316003.5 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_6
792 | Available | Input Register | U1 string failure branch 7 | Boolean | 16002 | 6 | 316003.6 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_7
793 | Available | Input Register | U1 string failure branch 8 | Boolean | 16002 | 7 | 316003.7 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U1_string_failure_branch_8
794 | Available | Input Register | U2 string failure branch 1 | Boolean | 16002 | 8 | 316003.8 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_1
795 | Available | Input Register | U2 string failure branch 2 | Boolean | 16002 | 9 | 316003.9 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_2
796 | Available | Input Register | U2 string failure branch 3 | Boolean | 16002 | 10 | 316003.10 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_3
797 | Available | Input Register | U2 string failure branch 4 | Boolean | 16002 | 11 | 316003.11 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_4
798 | Available | Input Register | U2 string failure branch 5 | Boolean | 16002 | 12 | 316003.12 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_5
799 | Available | Input Register | U2 string failure branch 6 | Boolean | 16002 | 13 | 316003.13 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_6
800 | Available | Input Register | U2 string failure branch 7 | Boolean | 16002 | 14 | 316003.14 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_7
801 | Available | Input Register | U2 string failure branch 8 | Boolean | 16002 | 15 | 316003.15 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U2_string_failure_branch_8
802 | Available | Input Register | U3 string failure branch 1 | Boolean | 16002 | 16 | 316003.16 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_1
803 | Available | Input Register | U3 string failure branch 2 | Boolean | 16002 | 17 | 316003.17 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_2
804 | Available | Input Register | U3 string failure branch 3 | Boolean | 16002 | 18 | 316003.18 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_3
805 | Available | Input Register | U3 string failure branch 4 | Boolean | 16002 | 19 | 316003.19 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_4
806 | Available | Input Register | U3 string failure branch 5 | Boolean | 16002 | 20 | 316003.20 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_5
807 | Available | Input Register | U3 string failure branch 6 | Boolean | 16002 | 21 | 316003.21 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_6
808 | Available | Input Register | U3 string failure branch 7 | Boolean | 16002 | 22 | 316003.22 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_7
809 | Available | Input Register | U3 string failure branch 8 | Boolean | 16002 | 23 | 316003.23 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U3_string_failure_branch_8
810 | Available | Input Register | U4 string failure branch 1 | Boolean | 16002 | 24 | 316003.24 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_1
811 | Available | Input Register | U4 string failure branch 2 | Boolean | 16002 | 25 | 316003.25 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_2
812 | Available | Input Register | U4 string failure branch 3 | Boolean | 16002 | 26 | 316003.26 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_3
813 | Available | Input Register | U4 string failure branch 4 | Boolean | 16002 | 27 | 316003.27 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_4
814 | Available | Input Register | U4 string failure branch 5 | Boolean | 16002 | 28 | 316003.28 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_5
815 | Available | Input Register | U4 string failure branch 6 | Boolean | 16002 | 29 | 316003.29 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_6
816 | Available | Input Register | U4 string failure branch 7 | Boolean | 16002 | 30 | 316003.30 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_7
817 | Available | Input Register | U4 string failure branch 8 | Boolean | 16002 | 31 | 316003.31 |  | On (1) | Alarm | Normal | [10 empty] | IREG_16002_U4_string_failure_branch_8
818 | Available | Input Register | U1 Warning Number of Strings Branch 1 | 16-bit unsigned integer | 16004 |  | 316005 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16004_U1_Warning_Number_of_Strings_Branch_1_count
819 | Available | Input Register | U1 Warning Number of Strings Branch 2 | 16-bit unsigned integer | 16005 |  | 316006 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16005_U1_Warning_Number_of_Strings_Branch_2_count
820 | Available | Input Register | U1 Warning Number of Strings Branch 3 | 16-bit unsigned integer | 16006 |  | 316007 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16006_U1_Warning_Number_of_Strings_Branch_3_count
821 | Available | Input Register | U1 Warning Number of Strings Branch 4 | 16-bit unsigned integer | 16007 |  | 316008 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16007_U1_Warning_Number_of_Strings_Branch_4_count
822 | Available | Input Register | U1 Warning Number of Strings Branch 5 | 16-bit unsigned integer | 16008 |  | 316009 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16008_U1_Warning_Number_of_Strings_Branch_5_count
823 | Available | Input Register | U1 Warning Number of Strings Branch 6 | 16-bit unsigned integer | 16009 |  | 316010 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16009_U1_Warning_Number_of_Strings_Branch_6_count
824 | Available | Input Register | U1 Warning Number of Strings Branch 7 | 16-bit unsigned integer | 16010 |  | 316011 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16010_U1_Warning_Number_of_Strings_Branch_7_count
825 | Available | Input Register | U2 Warning Number of Strings Branch 1 | 16-bit unsigned integer | 16020 |  | 316021 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16020_U2_Warning_Number_of_Strings_Branch_1_count
826 | Available | Input Register | U2 Warning Number of Strings Branch 2 | 16-bit unsigned integer | 16021 |  | 316022 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16021_U2_Warning_Number_of_Strings_Branch_2_count
827 | Available | Input Register | U2 Warning Number of Strings Branch 3 | 16-bit unsigned integer | 16022 |  | 316023 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16022_U2_Warning_Number_of_Strings_Branch_3_count
828 | Available | Input Register | U2 Warning Number of Strings Branch 4 | 16-bit unsigned integer | 16023 |  | 316024 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16023_U2_Warning_Number_of_Strings_Branch_4_count
829 | Available | Input Register | U2 Warning Number of Strings Branch 5 | 16-bit unsigned integer | 16024 |  | 316025 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16024_U2_Warning_Number_of_Strings_Branch_5_count
830 | Available | Input Register | U2 Warning Number of Strings Branch 6 | 16-bit unsigned integer | 16025 |  | 316026 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16025_U2_Warning_Number_of_Strings_Branch_6_count
831 | Available | Input Register | U2 Warning Number of Strings Branch 7 | 16-bit unsigned integer | 16026 |  | 316027 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16026_U2_Warning_Number_of_Strings_Branch_7_count
832 | Available | Input Register | U3 Warning Number of Strings Branch 1 | 16-bit unsigned integer | 16036 |  | 316037 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16036_U3_Warning_Number_of_Strings_Branch_1_count
833 | Available | Input Register | U3 Warning Number of Strings Branch 2 | 16-bit unsigned integer | 16037 |  | 316038 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16037_U3_Warning_Number_of_Strings_Branch_2_count
834 | Available | Input Register | U3 Warning Number of Strings Branch 3 | 16-bit unsigned integer | 16038 |  | 316039 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16038_U3_Warning_Number_of_Strings_Branch_3_count
835 | Available | Input Register | U3 Warning Number of Strings Branch 4 | 16-bit unsigned integer | 16039 |  | 316040 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16039_U3_Warning_Number_of_Strings_Branch_4_count
836 | Available | Input Register | U3 Warning Number of Strings Branch 5 | 16-bit unsigned integer | 16040 |  | 316041 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16040_U3_Warning_Number_of_Strings_Branch_5_count
837 | Available | Input Register | U3 Warning Number of Strings Branch 6 | 16-bit unsigned integer | 16041 |  | 316042 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16041_U3_Warning_Number_of_Strings_Branch_6_count
838 | Available | Input Register | U3 Warning Number of Strings Branch 7 | 16-bit unsigned integer | 16042 |  | 316043 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16042_U3_Warning_Number_of_Strings_Branch_7_count
839 | Available | Input Register | U4 Warning Number of Strings Branch 1 | 16-bit unsigned integer | 16052 |  | 316053 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16052_U4_Warning_Number_of_Strings_Branch_1_count
840 | Available | Input Register | U4 Warning Number of Strings Branch 2 | 16-bit unsigned integer | 16053 |  | 316054 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16053_U4_Warning_Number_of_Strings_Branch_2_count
841 | Available | Input Register | U4 Warning Number of Strings Branch 3 | 16-bit unsigned integer | 16054 |  | 316055 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16054_U4_Warning_Number_of_Strings_Branch_3_count
842 | Available | Input Register | U4 Warning Number of Strings Branch 4 | 16-bit unsigned integer | 16055 |  | 316056 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16055_U4_Warning_Number_of_Strings_Branch_4_count
843 | Available | Input Register | U4 Warning Number of Strings Branch 5 | 16-bit unsigned integer | 16056 |  | 316057 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16056_U4_Warning_Number_of_Strings_Branch_5_count
844 | Available | Input Register | U4 Warning Number of Strings Branch 6 | 16-bit unsigned integer | 16057 |  | 316058 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16057_U4_Warning_Number_of_Strings_Branch_6_count
845 | Available | Input Register | U4 Warning Number of Strings Branch 7 | 16-bit unsigned integer | 16058 |  | 316059 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | IREG_16058_U4_Warning_Number_of_Strings_Branch_7_count
846 | Available | Holding Register | Set system clock year | 16-bit unsigned integer | 14999 |  | 415000 |  |  |  |  | year | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_14999_Set_system_clock_year_year |  | This point is not mapped to ignition
847 | Available | Holding Register | Set system clock month | 16-bit unsigned integer | 15000 |  | 415001 |  |  |  |  | month | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15000_Set_system_clock_month_month |  | This point is not mapped to ignition
848 | Available | Holding Register | Set system clock day | 16-bit unsigned integer | 15001 |  | 415002 |  |  |  |  | day | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15001_Set_system_clock_day_day |  | This point is not mapped to ignition
849 | Available | Holding Register | Set system clock hour | 16-bit unsigned integer | 15002 |  | 415003 |  |  |  |  | hr | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15002_Set_system_clock_hour_hr |  | This point is not mapped to ignition
850 | Available | Holding Register | Set system clock minute | 16-bit unsigned integer | 15003 |  | 415004 |  |  |  |  | min | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15003_Set_system_clock_minute_min |  | This point is not mapped to ignition
851 | Available | Holding Register | Set system clock second | 16-bit unsigned integer | 15004 |  | 415005 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15004_Set_system_clock_second_s |  | This point is not mapped to ignition
852 | Available | Holding Register | Start stop command | Enumeration | 15005 |  | 415006 | [14 empty] | HREG_15005_Start_stop_command | 16#CE to 16#CF
853 | Available | Holding Register | Emergency stop command | Enumeration | 15006 |  | 415007 | [14 empty] | HREG_15006_Emergency_stop_command | 16#CE to 16#CF
854 | Available | Holding Register | Active power percent | 16-bit unsigned integer | 15007 |  | 415008 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15007_Active_power_percent_pct |  | This point is not mapped to ignition
855 | Available | Holding Register | Local remote control | Enumeration | 15009 |  | 415010 | [14 empty] | HREG_15009_Local_remote_control | 0 to 1 | This point is not mapped to ignition
856 | Available | Holding Register | Reactive power mode | Enumeration | 15010 |  | 415011 | [14 empty] | HREG_15010_Reactive_power_mode | 16#55,16#A1 to 16#A5
857 | Available | Holding Register | Reactive power percent setpoint | 16-bit signed integer | 15011 |  | 415012 |  |  |  |  | % | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15011_Reactive_power_percent_setpoint_pct |  | This point is not mapped to ignition
858 | Available | Holding Register | Power factor setpoint | 16-bit signed integer | 15012 |  | 415013 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15012_Power_factor_setpoint_PU
859 | Available | Holding Register | Power limit actual value setpoint | 16-bit unsigned integer | 15013 |  | 415014 |  |  |  |  | kW | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15013_Power_limit_actual_value_setpoint_kW
860 | Available | Holding Register | Reactive power actual limit setpoint | 16-bit signed integer | 15014 |  | 415015 |  |  |  |  | kvar | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15014_Reactive_power_actual_limit_setpoint_kvar
861 | Available | Holding Register | Active power ramp up rate setpoint | 16-bit unsigned integer | 15015 |  | 415016 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15015_Active_power_ramp_up_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
862 | Available | Holding Register | Active power ramp down rate setpoint | 16-bit unsigned integer | 15016 |  | 415017 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15016_Active_power_ramp_down_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
863 | Available | Holding Register | Stop delay time | 16-bit unsigned integer | 15019 |  | 415020 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15019_Stop_delay_time_s |  | This point is not mapped to ignition
864 | Available | Holding Register | Stop slope | 16-bit unsigned integer | 15020 |  | 415021 |  |  |  |  | %/s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15020_Stop_slope_pct_per_s |  | This point is not mapped to ignition
865 | Available | Holding Register | U1 on off command | Enumeration | 15021 |  | 415022 | [14 empty] | HREG_15021_U1_on_off_command | 16#CE to 16#CF
866 | Available | Holding Register | U2 on off command | Enumeration | 15022 |  | 415023 | [14 empty] | HREG_15022_U2_on_off_command | 16#CE to 16#CF
867 | Available | Holding Register | U3 on off command | Enumeration | 15023 |  | 415024 | [14 empty] | HREG_15023_U3_on_off_command | 16#CE to 16#CF
868 | Available | Holding Register | U4 on off command | Enumeration | 15024 |  | 415025 | [14 empty] | HREG_15024_U4_on_off_command | 16#CE to 16#CF
869 | Available | Holding Register | High voltage load switch remote open | 16-bit unsigned integer | 15025 |  | 415026 |  |  | Tripped | Normal | boolean |  | 0 | 65535 | [6 empty] | HREG_15025_High_voltage_load_switch_remote_open_boolean |  | This point is not mapped to ignition
870 | Available | Holding Register | Reactive power ramp up rate setpoint | 16-bit unsigned integer | 15026 |  | 415027 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15026_Reactive_power_ramp_up_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
871 | Available | Holding Register | Reactive power ramp down rate setpoint | 16-bit unsigned integer | 15027 |  | 415028 |  |  |  |  | %/s | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15027_Reactive_power_ramp_down_rate_setpoint_pct_per_s |  | This point is not mapped to ignition
872 | Available | Holding Register | Qu activation power point | 16-bit unsigned integer | 15028 |  | 415029 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15028_Qu_activation_power_point_pct |  | This point is not mapped to ignition
873 | Available | Holding Register | Qu operation mode | Enumeration | 15029 |  | 415030 | [14 empty] | HREG_15029_Qu_operation_mode | 16#A1 to 16#A3 | This point is not mapped to ignition
874 | Available | Holding Register | Qu input voltage source | Enumeration | 15030 |  | 415031 | [14 empty] | HREG_15030_Qu_input_voltage_source | 16#B1 to 16#B2 | This point is not mapped to ignition
875 | Available | Holding Register | Qu reactive reactive power limit setpoint | 16-bit unsigned integer | 15031 |  | 415032 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15031_Qu_reactive_reactive_power_limit_setpoint_pct |  | This point is not mapped to ignition
876 | Available | Holding Register | Qu reactive reactive power limit setpoint | 16-bit unsigned integer | 15032 |  | 415033 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15032_Qu_reactive_reactive_power_limit_setpoint_pct |  | This point is not mapped to ignition
877 | Available | Holding Register | Qu power factor end point | 16-bit unsigned integer | 15033 |  | 415034 |  |  |  |  | PU | 1000 | 0 | 65535 | 0 | 65.535 |  |  |  |  | HREG_15033_Qu_power_factor_end_point_PU |  | This point is not mapped to ignition
878 | Available | Holding Register | Qu power factor start point | 16-bit unsigned integer | 15034 |  | 415035 |  |  |  |  | PU | 1000 | 0 | 65535 | 0 | 65.535 |  |  |  |  | HREG_15034_Qu_power_factor_start_point_PU |  | This point is not mapped to ignition
879 | Available | Holding Register | Qu voltage rise start point | 16-bit unsigned integer | 15036 |  | 415037 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15036_Qu_voltage_rise_start_point_pct |  | This point is not mapped to ignition
880 | Available | Holding Register | Qu voltage rise end point | 16-bit unsigned integer | 15037 |  | 415038 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15037_Qu_voltage_rise_end_point_pct |  | This point is not mapped to ignition
881 | Available | Holding Register | Qu voltage drop start point | 16-bit unsigned integer | 15038 |  | 415039 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15038_Qu_voltage_drop_start_point_pct |  | This point is not mapped to ignition
882 | Available | Holding Register | Qu voltage drop end point | 16-bit unsigned integer | 15039 |  | 415040 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15039_Qu_voltage_drop_end_point_pct |  | This point is not mapped to ignition
883 | Available | Holding Register | HV load switch remote close | Enumeration | 15048 |  | 415049 |  |  | Closed | Open | [10 empty] | HREG_15048_HV_load_switch_remote_close | 0 to 1
884 | Available | Holding Register | Qu reactive power rising start | 16-bit signed integer | 15050 |  | 415051 |  |  |  |  | % | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15050_Qu_reactive_power_rising_start_pct |  | This point is not mapped to ignition
885 | Available | Holding Register | Qu reactive power decline start | 16-bit signed integer | 15051 |  | 415052 |  |  |  |  | % | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  |  |  | HREG_15051_Qu_reactive_power_decline_start_pct |  | This point is not mapped to ignition
886 | Available | Holding Register | Enable pu | Enumeration | 15054 |  | 415055 | [14 empty] | HREG_15054_Enable_pu | 16#55,16#AA | This point is not mapped to ignition
887 | Available | Holding Register | Pu active power rising gradiant | 16-bit unsigned integer | 15055 |  | 415056 |  |  |  |  | % | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15055_Pu_active_power_rising_gradiant_pct |  | This point is not mapped to ignition
888 | Available | Holding Register | Pu active power decline gradiant | 16-bit unsigned integer | 15056 |  | 415057 |  |  |  |  | % | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15056_Pu_active_power_decline_gradiant_pct |  | This point is not mapped to ignition
889 | Available | Holding Register | Dc switch open close | Enumeration | 15059 |  | 415060 | [14 empty] | HREG_15059_Dc_switch_open_close | 16#55,16#AA
890 | Available | Holding Register | Night svg enable disable | Enumeration | 15060 |  | 415061 | [14 empty] | HREG_15060_Night_svg_enable_disable | 16#55,16#AA | This point is not mapped to ignition
891 | Available | Holding Register | Start waiting time | 16-bit unsigned integer | 15061 |  | 415062 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15061_Start_waiting_time_s |  | This point is not mapped to ignition
892 | Available | Holding Register | Time for automatic recovery from fault | 16-bit unsigned integer | 15062 |  | 415063 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15062_Time_for_automatic_recovery_from_fault_s |  | This point is not mapped to ignition
893 | Available | Holding Register | Overfrequency recovery threshold | 16-bit unsigned integer | 15063 |  | 415064 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15063_Overfrequency_recovery_threshold_Hz |  | This point is not mapped to ignition
894 | Available | Holding Register | Underfrequency recovery threshold | 16-bit unsigned integer | 15064 |  | 415065 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15064_Underfrequency_recovery_threshold_Hz |  | This point is not mapped to ignition
895 | Available | Holding Register | Dc starting voltage | 16-bit unsigned integer | 15065 |  | 415066 |  |  |  |  | V | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15065_Dc_starting_voltage_V |  | This point is not mapped to ignition
896 | Available | Holding Register | Frequency modulation enable | Enumeration | 15072 |  | 415073 | [14 empty] | HREG_15072_Frequency_modulation_enable | 16#55,16#AA | This point is not mapped to ignition
897 | Available | Holding Register | Overfrequency derating start point | 16-bit unsigned integer | 15074 |  | 415075 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15074_Overfrequency_derating_start_point_Hz |  | This point is not mapped to ignition
898 | Available | Holding Register | Overfrequency derating end point | 16-bit unsigned integer | 15075 |  | 415076 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15075_Overfrequency_derating_end_point_Hz |  | This point is not mapped to ignition
899 | Available | Holding Register | Overfrequency derating factor | 16-bit unsigned integer | 15076 |  | 415077 |  |  |  |  | PU | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15076_Overfrequency_derating_factor_PU |  | This point is not mapped to ignition
900 | Available | Holding Register | Overfrequency derating limit | 16-bit unsigned integer | 15077 |  | 415078 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15077_Overfrequency_derating_limit_pct |  | This point is not mapped to ignition
901 | Available | Holding Register | Frequency regulation input source | Enumeration | 15078 |  | 415079 | [14 empty] | HREG_15078_Frequency_regulation_input_source | 16#B1 to 16#B2 | This point is not mapped to ignition
902 | Available | Holding Register | Frequency regulation active power | 16-bit unsigned integer | 15079 |  | 415080 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15079_Frequency_regulation_active_power_pct |  | This point is not mapped to ignition
903 | Available | Holding Register | Underfrequency rising start point | 16-bit unsigned integer | 15080 |  | 415081 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15080_Underfrequency_rising_start_point_Hz |  | This point is not mapped to ignition
904 | Available | Holding Register | Underfrequency rising end point | 16-bit unsigned integer | 15081 |  | 415082 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15081_Underfrequency_rising_end_point_Hz |  | This point is not mapped to ignition
905 | Available | Holding Register | Underfrequency rise factor | 16-bit unsigned integer | 15082 |  | 415083 |  |  |  |  | PU | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15082_Underfrequency_rise_factor_PU |  | This point is not mapped to ignition
906 | Available | Holding Register | Underfrequency rising limit | 16-bit unsigned integer | 15083 |  | 415084 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15083_Underfrequency_rising_limit_pct |  | This point is not mapped to ignition
907 | Available | Holding Register | Leakage current protection value | 16-bit unsigned integer | 15087 |  | 415088 |  |  |  |  | A | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15087_Leakage_current_protection_value_A |  | This point is not mapped to ignition
908 | Available | Holding Register | Insulation monitoring protection threshold | 16-bit unsigned integer | 15115 |  | 415116 |  |  |  |  | kΩ | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15115_Insulation_monitoring_protection_threshold_kΩ
909 | Available | Holding Register | Ac overvoltage level 1 protection | 16-bit unsigned integer | 15119 |  | 415120 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15119_Ac_overvoltage_level_1_protection_pct |  | This point is not mapped to ignition
910 | Available | Holding Register | Ac overvoltage level 2 protection | 16-bit unsigned integer | 15120 |  | 415121 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15120_Ac_overvoltage_level_2_protection_pct |  | This point is not mapped to ignition
911 | Available | Holding Register | Ac overvoltage level 3 protection | 16-bit unsigned integer | 15121 |  | 415122 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15121_Ac_overvoltage_level_3_protection_pct |  | This point is not mapped to ignition
912 | Available | Holding Register | Ac overvoltage level 4 protection | 16-bit unsigned integer | 15122 |  | 415123 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15122_Ac_overvoltage_level_4_protection_pct |  | This point is not mapped to ignition
913 | Available | Holding Register | Ac overvoltage level 5 protection | 16-bit unsigned integer | 15123 |  | 415124 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15123_Ac_overvoltage_level_5_protection_pct |  | This point is not mapped to ignition
914 | Available | Holding Register | Vmax recover | 16-bit unsigned integer | 15129 |  | 415130 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15129_Vmax_recover_pct |  | This point is not mapped to ignition
915 | Available | Holding Register | Ac undervoltage level 1 protection | 16-bit unsigned integer | 15130 |  | 415131 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15130_Ac_undervoltage_level_1_protection_pct |  | This point is not mapped to ignition
916 | Available | Holding Register | Ac undervoltage level 2 protection | 16-bit unsigned integer | 15131 |  | 415132 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15131_Ac_undervoltage_level_2_protection_pct |  | This point is not mapped to ignition
917 | Available | Holding Register | Ac undervoltage level 3 protection | 16-bit unsigned integer | 15132 |  | 415133 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15132_Ac_undervoltage_level_3_protection_pct |  | This point is not mapped to ignition
918 | Available | Holding Register | Ac undervoltage level 4 protection | 16-bit unsigned integer | 15133 |  | 415134 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15133_Ac_undervoltage_level_4_protection_pct |  | This point is not mapped to ignition
919 | Available | Holding Register | Ac undervoltage level 5 protection | 16-bit unsigned integer | 15134 |  | 415135 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15134_Ac_undervoltage_level_5_protection_pct |  | This point is not mapped to ignition
920 | Available | Holding Register | Vmin recover | 16-bit unsigned integer | 15140 |  | 415141 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15140_Vmin_recover_pct |  | This point is not mapped to ignition
921 | Available | Holding Register | Grid over frequency level 1 protection | 16-bit unsigned integer | 15141 |  | 415142 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15141_Grid_over_frequency_level_1_protection_Hz |  | This point is not mapped to ignition
922 | Available | Holding Register | Grid over frequency level 2 protection | 16-bit unsigned integer | 15142 |  | 415143 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15142_Grid_over_frequency_level_2_protection_Hz |  | This point is not mapped to ignition
923 | Available | Holding Register | Grid over frequency level 3 protection | 16-bit unsigned integer | 15143 |  | 415144 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15143_Grid_over_frequency_level_3_protection_Hz |  | This point is not mapped to ignition
924 | Available | Holding Register | Grid over frequency level 4 protection | 16-bit unsigned integer | 15144 |  | 415145 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15144_Grid_over_frequency_level_4_protection_Hz |  | This point is not mapped to ignition
925 | Available | Holding Register | Grid over frequency level 5 protection | 16-bit unsigned integer | 15145 |  | 415146 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15145_Grid_over_frequency_level_5_protection_Hz |  | This point is not mapped to ignition
926 | Available | Holding Register | Fmax recover | 16-bit unsigned integer | 15151 |  | 415152 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15151_Fmax_recover_Hz |  | This point is not mapped to ignition
927 | Available | Holding Register | AC under frequency level 1 protection | 16-bit unsigned integer | 15152 |  | 415153 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15152_AC_under_frequency_level_1_protection_Hz |  | This point is not mapped to ignition
928 | Available | Holding Register | AC under frequency level 2 protection | 16-bit unsigned integer | 15153 |  | 415154 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15153_AC_under_frequency_level_2_protection_Hz |  | This point is not mapped to ignition
929 | Available | Holding Register | AC under frequency level 3 protection | 16-bit unsigned integer | 15154 |  | 415155 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15154_AC_under_frequency_level_3_protection_Hz |  | This point is not mapped to ignition
930 | Available | Holding Register | AC under frequency level 4 protection | 16-bit unsigned integer | 15155 |  | 415156 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15155_AC_under_frequency_level_4_protection_Hz |  | This point is not mapped to ignition
931 | Available | Holding Register | AC under frequency level 5 protection | 16-bit unsigned integer | 15156 |  | 415157 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15156_AC_under_frequency_level_5_protection_Hz |  | This point is not mapped to ignition
932 | Available | Holding Register | Fmin recover | 16-bit unsigned integer | 15162 |  | 415163 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15162_Fmin_recover_Hz |  | This point is not mapped to ignition
933 | Available | Holding Register | Floating mode | 16-bit unsigned integer | 15167 |  | 415168 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15167_Floating_mode_Hz |  | This point is not mapped to ignition
934 | Available | Holding Register | Over voltage level 1 trip time | 32-bit unsigned integer | 15169 |  | 415170 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15169_Over_voltage_level_1_trip_time_ms |  | This point is not mapped to ignition
935 | Available | Holding Register | Over voltage level 2 trip time | 16-bit unsigned integer | 15171 |  | 415172 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15171_Over_voltage_level_2_trip_time_ms |  | This point is not mapped to ignition
936 | Available | Holding Register | Over voltage level 3 trip time | 32-bit unsigned integer | 15173 |  | 415174 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15173_Over_voltage_level_3_trip_time_ms |  | This point is not mapped to ignition
937 | Available | Holding Register | Over voltage level 4 trip time | 16-bit unsigned integer | 15175 |  | 415176 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15175_Over_voltage_level_4_trip_time_ms |  | This point is not mapped to ignition
938 | Available | Holding Register | Over voltage level 5 trip time | 32-bit unsigned integer | 15177 |  | 415178 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15177_Over_voltage_level_5_trip_time_ms |  | This point is not mapped to ignition
939 | Available | Holding Register | Under voltage level 1 trip time | 16-bit unsigned integer | 15179 |  | 415180 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15179_Under_voltage_level_1_trip_time_ms |  | This point is not mapped to ignition
940 | Available | Holding Register | Under voltage level 2 trip time | 32-bit unsigned integer | 15181 |  | 415182 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15181_Under_voltage_level_2_trip_time_ms |  | This point is not mapped to ignition
941 | Available | Holding Register | Under voltage level 3 trip time | 16-bit unsigned integer | 15183 |  | 415184 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15183_Under_voltage_level_3_trip_time_ms |  | This point is not mapped to ignition
942 | Available | Holding Register | Under voltage level 4 trip time | 32-bit unsigned integer | 15185 |  | 415186 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15185_Under_voltage_level_4_trip_time_ms |  | This point is not mapped to ignition
943 | Available | Holding Register | Under voltage level 5 trip time | 16-bit unsigned integer | 15187 |  | 415188 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15187_Under_voltage_level_5_trip_time_ms |  | This point is not mapped to ignition
944 | Available | Holding Register | Over frequency level 1 trip time | 32-bit unsigned integer | 15189 |  | 415190 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15189_Over_frequency_level_1_trip_time_ms |  | This point is not mapped to ignition
945 | Available | Holding Register | Over frequency level 2 trip time | 32-bit unsigned integer | 15191 |  | 415192 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15191_Over_frequency_level_2_trip_time_ms |  | This point is not mapped to ignition
946 | Available | Holding Register | Over frequency level 3 trip time | 32-bit unsigned integer | 15193 |  | 415194 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15193_Over_frequency_level_3_trip_time_ms |  | This point is not mapped to ignition
947 | Available | Holding Register | Over frequency level 4 trip time | 32-bit unsigned integer | 15195 |  | 415196 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15195_Over_frequency_level_4_trip_time_ms |  | This point is not mapped to ignition
948 | Available | Holding Register | Over frequency level 5 trip time | 32-bit unsigned integer | 15197 |  | 415198 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15197_Over_frequency_level_5_trip_time_ms |  | This point is not mapped to ignition
949 | Available | Holding Register | Under frequency level 1 trip time | 32-bit unsigned integer | 15199 |  | 415200 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15199_Under_frequency_level_1_trip_time_ms |  | This point is not mapped to ignition
950 | Available | Holding Register | Under frequency level 2 trip time | 32-bit unsigned integer | 15201 |  | 415202 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15201_Under_frequency_level_2_trip_time_ms |  | This point is not mapped to ignition
951 | Available | Holding Register | Under frequency level 3 trip time | 32-bit unsigned integer | 15203 |  | 415204 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15203_Under_frequency_level_3_trip_time_ms |  | This point is not mapped to ignition
952 | Available | Holding Register | Under frequency level 4 trip time | 32-bit unsigned integer | 15205 |  | 415206 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15205_Under_frequency_level_4_trip_time_ms |  | This point is not mapped to ignition
953 | Available | Holding Register | Under frequency level 5 trip time | 32-bit unsigned integer | 15207 |  | 415208 |  |  |  |  | ms | 0.05 | 0 | 4294967295 | 0 | 85899345900 |  |  |  |  | HREG_15207_Under_frequency_level_5_trip_time_ms |  | This point is not mapped to ignition
954 | Available | Holding Register | Active power control closed loop enable disable | Enumeration | 15211 |  | 415212 | [14 empty] | HREG_15211_Active_power_control_closed_loop_enable_disable | 16#55,16#AA | This point is not mapped to ignition
955 | Available | Holding Register | Reactive power control closed loop enable disable | Enumeration | 15212 |  | 415213 | [14 empty] | HREG_15212_Reactive_power_control_closed_loop_enable_disable | 16#55,16#AA | This point is not mapped to ignition
956 | Available | Holding Register | Overfrequency derating output variation baseline | Enumeration | 15221 |  | 415222 | [14 empty] | HREG_15221_Overfrequency_derating_output_variation_baseline | 16#A1-16#A4
957 | Available | Holding Register | Underfrequency rising output change base | Enumeration | 15222 |  | 415223 | [14 empty] | HREG_15222_Underfrequency_rising_output_change_base | 16#A1-16#A4
958 | Available | Holding Register | Reactive power response time | 16-bit unsigned integer | 15223 |  | 415224 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15223_Reactive_power_response_time_s |  | This point is not mapped to ignition
959 | Available | Holding Register | QP_K1 | 16-bit signed integer | 15224 |  | 415225 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15224_QP_K1_PU |  | This point is not mapped to ignition
960 | Available | Holding Register | QP_K2 | 16-bit signed integer | 15225 |  | 415226 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15225_QP_K2_PU |  | This point is not mapped to ignition
961 | Available | Holding Register | QP_K3 | 16-bit signed integer | 15226 |  | 415227 |  |  |  |  | PU | 1000 | -32768 | 32767 | -32.768 | 32.767 |  |  |  |  | HREG_15226_QP_K3_PU |  | This point is not mapped to ignition
962 | Available | Holding Register | QP_P1 | 16-bit unsigned integer | 15227 |  | 415228 |  |  |  |  | PU | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15227_QP_P1_PU |  | This point is not mapped to ignition
963 | Available | Holding Register | QP_P2 | 16-bit unsigned integer | 15228 |  | 415229 |  |  |  |  | PU | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15228_QP_P2_PU |  | This point is not mapped to ignition
964 | Available | Holding Register | QP_P3 | 16-bit unsigned integer | 15229 |  | 415230 |  |  |  |  | PU | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15229_QP_P3_PU |  | This point is not mapped to ignition
965 | Available | Holding Register | QP mode | Enumeration | 15230 |  | 415231 | [14 empty] | HREG_15230_QP_mode | 16#A1 to 16#A2 | This point is not mapped to ignition
966 | Available | Holding Register | Heartbeat timeout period | 16-bit unsigned integer | 15248 |  | 415249 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15248_Heartbeat_timeout_period_s |  | This point is not mapped to ignition
967 | Available | Holding Register | Grid connection maximum voltage | 16-bit unsigned integer | 15256 |  | 415257 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15256_Grid_connection_maximum_voltage_pct |  | This point is not mapped to ignition
968 | Available | Holding Register | Grid connection minimum voltage | 16-bit unsigned integer | 15257 |  | 415258 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15257_Grid_connection_minimum_voltage_pct |  | This point is not mapped to ignition
969 | Available | Holding Register | Grid connection maximum frequency | 16-bit unsigned integer | 15258 |  | 415259 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15258_Grid_connection_maximum_frequency_Hz |  | This point is not mapped to ignition
970 | Available | Holding Register | Grid connection minimum frequency | 16-bit unsigned integer | 15259 |  | 415260 |  |  |  |  | Hz | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_15259_Grid_connection_minimum_frequency_Hz |  | This point is not mapped to ignition
971 | Available | Holding Register | Grid detection before connection | 16-bit unsigned integer | 15260 |  | 415261 | [6 empty] | 0 | 65535 | [6 empty] | HREG_15260_Grid_detection_before_connection |  | This point is not mapped to ignition
972 | Available | Holding Register | Boot waiting time | 16-bit unsigned integer | 15261 |  | 415262 | [6 empty] | 0 | 65535 | [6 empty] | HREG_15261_Boot_waiting_time |  | This point is not mapped to ignition
973 |  | Holding Register | Active power soft start | 16-bit unsigned integer | 15262 |  | 415263 |  |  | Enabled | Disabled |  |  | 0 | 65535 | [6 empty] | HREG_15262_Active_power_soft_start | 0 to 1
974 |  | Holding Register | Reactive power soft start | 16-bit unsigned integer | 15263 |  | 415264 |  |  | Enabled | Disabled |  |  | 0 | 65535 | [6 empty] | HREG_15263_Reactive_power_soft_start | 0 to 1
975 | Available | Holding Register | Specified overexcitation PF | 16-bit signed integer | 15264 |  | 415265 | [6 empty] | -32768 | 32767 | [6 empty] | HREG_15264_Specified_overexcitation_PF |  | This point is not mapped to ignition
976 | Available | Holding Register | Specified underrexcitation PF | 16-bit signed integer | 15265 |  | 415266 | [6 empty] | -32768 | 32767 | [6 empty] | HREG_15265_Specified_underrexcitation_PF |  | This point is not mapped to ignition
977 | Available | Holding Register | QU reference voltage automatic adjustment | 16-bit unsigned integer | 15266 |  | 415267 | [6 empty] | 0 | 65535 | [6 empty] | HREG_15266_QU_reference_voltage_automatic_adjustment |  | This point is not mapped to ignition
978 | Available | Holding Register | QU reference voltage adjustment | 16-bit unsigned integer | 15267 |  | 415268 | [6 empty] | 0 | 65535 | [6 empty] | HREG_15267_QU_reference_voltage_adjustment |  | This point is not mapped to ignition
979 | Available | Holding Register | QU reference voltage automatic adjustment time | 16-bit unsigned integer | 15268 |  | 415269 | [6 empty] | 0 | 65535 | [6 empty] | HREG_15268_QU_reference_voltage_automatic_adjustment_time |  | This point is not mapped to ignition
980 | Available | Holding Register | Overvoltage derating start point | 16-bit unsigned integer | 15269 |  | 415270 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15269_Overvoltage_derating_start_point_pct |  | This point is not mapped to ignition
981 | Available | Holding Register | Overvoltage derating power start point | 16-bit unsigned integer | 15270 |  | 415271 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15270_Overvoltage_derating_power_start_point_pct |  | This point is not mapped to ignition
982 | Available | Holding Register | Overvoltage derating end point | 16-bit unsigned integer | 15271 |  | 415272 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15271_Overvoltage_derating_end_point_pct |  | This point is not mapped to ignition
983 | Available | Holding Register | Overvoltage derating power end point | 16-bit unsigned integer | 15272 |  | 415273 |  |  |  |  | % | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15272_Overvoltage_derating_power_end_point_pct |  | This point is not mapped to ignition
984 | Available | Holding Register | Voltage derating response time | 16-bit unsigned integer | 15273 |  | 415274 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15273_Voltage_derating_response_time_s |  | This point is not mapped to ignition
985 | Available | Holding Register | Over frequency response time | 16-bit unsigned integer | 15274 |  | 415275 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15274_Over_frequency_response_time_s |  | This point is not mapped to ignition
986 | Available | Holding Register | Under frequency response time | 16-bit unsigned integer | 15275 |  | 415276 |  |  |  |  | s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15275_Under_frequency_response_time_s |  | This point is not mapped to ignition
987 | Available | Holding Register | Over frequency response delay time | 16-bit unsigned integer | 15280 |  | 415281 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15280_Over_frequency_response_delay_time_ms |  | This point is not mapped to ignition
988 | Available | Holding Register | Under frequency response delay time | 16-bit unsigned integer | 15281 |  | 415282 |  |  |  |  | ms | 0.05 | 0 | 65535 | 0 | 1310700 |  |  |  |  | HREG_15281_Under_frequency_response_delay_time_ms |  | This point is not mapped to ignition
989 |  | Holding Register | Disconnection countdown time | 16-bit unsigned integer | 15305 |  | 415306 |  |  |  |  | s | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15305_Disconnection_countdown_time_s
990 |  | Holding Register | Number of disconnections | 16-bit unsigned integer | 15306 |  | 415307 | [5 empty] | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15306_Number_of_disconnections
991 |  | Holding Register | Disconnection time | 16-bit unsigned integer | 15307 |  | 415308 |  |  |  |  | ms | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15307_Disconnection_time_ms
992 |  | Holding Register | Shutdown slope at disconnections | 16-bit unsigned integer | 15308 |  | 415309 |  |  |  |  | %/s | 10 | 0 | 65535 | 0 | 6553.5 |  |  |  |  | HREG_15308_Shutdown_slope_at_disconnections_pct_per_s
993 | Available | Holding Register | Zone monitoring | 16-bit unsigned integer | 15799 |  | 415800 |  | State change | Enable | Disable | boolean |  | 0 | 65535 | [6 empty] | HREG_15799_Zone_monitoring_boolean |  | This point is not mapped to ignition
994 | Available | Holding Register | Sensitivity | 16-bit unsigned integer | 15801 |  | 415802 |  |  |  |  | unitless | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15801_Sensitivity |  | This point is not mapped to ignition
995 | Available | Holding Register | Clear zone monitor data | 16-bit unsigned integer | 15802 |  | 415803 |  | On (1) | Clear | No Action | boolean |  | 0 | 65535 | [6 empty] | HREG_15802_Clear_zone_monitor_data_boolean |  | This point is not mapped to ignition
996 | Available | Holding Register | Clear fault | 16-bit unsigned integer | 15803 |  | 415804 |  | On (1) | Clear | No Action | boolean |  | 0 | 65535 | [6 empty] | HREG_15803_Clear_fault_boolean |  | This point is not mapped to ignition
997 | Available | Holding Register | U1 number of strings on branch 1 | 16-bit unsigned integer | 15804 |  | 415805 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15804_U1_number_of_strings_on_branch_1_count |  | This point is not mapped to ignition
998 | Available | Holding Register | U1 number of strings on branch 2 | 16-bit unsigned integer | 15805 |  | 415806 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15805_U1_number_of_strings_on_branch_2_count |  | This point is not mapped to ignition
999 | Available | Holding Register | U1 number of strings on branch 3 | 16-bit unsigned integer | 15806 |  | 415807 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15806_U1_number_of_strings_on_branch_3_count |  | This point is not mapped to ignition
1000 | Available | Holding Register | U1 number of strings on branch 4 | 16-bit unsigned integer | 15807 |  | 415808 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15807_U1_number_of_strings_on_branch_4_count |  | This point is not mapped to ignition
1001 | Available | Holding Register | U1 number of strings on branch 5 | 16-bit unsigned integer | 15808 |  | 415809 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15808_U1_number_of_strings_on_branch_5_count |  | This point is not mapped to ignition
1002 | Available | Holding Register | U1 number of strings on branch 6 | 16-bit unsigned integer | 15809 |  | 415810 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15809_U1_number_of_strings_on_branch_6_count |  | This point is not mapped to ignition
1003 | Available | Holding Register | U1 number of strings on branch 7 | 16-bit unsigned integer | 15810 |  | 415811 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15810_U1_number_of_strings_on_branch_7_count |  | This point is not mapped to ignition
1004 | Available | Holding Register | U2 number of strings on branch 1 | 16-bit unsigned integer | 15820 |  | 415821 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15820_U2_number_of_strings_on_branch_1_count |  | This point is not mapped to ignition
1005 | Available | Holding Register | U2 number of strings on branch 2 | 16-bit unsigned integer | 15821 |  | 415822 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15821_U2_number_of_strings_on_branch_2_count |  | This point is not mapped to ignition
1006 | Available | Holding Register | U2 number of strings on branch 3 | 16-bit unsigned integer | 15822 |  | 415823 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15822_U2_number_of_strings_on_branch_3_count |  | This point is not mapped to ignition
1007 | Available | Holding Register | U2 number of strings on branch 4 | 16-bit unsigned integer | 15823 |  | 415824 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15823_U2_number_of_strings_on_branch_4_count |  | This point is not mapped to ignition
1008 | Available | Holding Register | U2 number of strings on branch 5 | 16-bit unsigned integer | 15824 |  | 415825 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15824_U2_number_of_strings_on_branch_5_count |  | This point is not mapped to ignition
1009 | Available | Holding Register | U2 number of strings on branch 6 | 16-bit unsigned integer | 15825 |  | 415826 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15825_U2_number_of_strings_on_branch_6_count |  | This point is not mapped to ignition
1010 | Available | Holding Register | U2 number of strings on branch 7 | 16-bit unsigned integer | 15826 |  | 415827 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15826_U2_number_of_strings_on_branch_7_count |  | This point is not mapped to ignition
1011 | Available | Holding Register | U3 number of strings on branch 1 | 16-bit unsigned integer | 15836 |  | 415837 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15836_U3_number_of_strings_on_branch_1_count |  | This point is not mapped to ignition
1012 | Available | Holding Register | U3 number of strings on branch 2 | 16-bit unsigned integer | 15837 |  | 415838 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15837_U3_number_of_strings_on_branch_2_count |  | This point is not mapped to ignition
1013 | Available | Holding Register | U3 number of strings on branch 3 | 16-bit unsigned integer | 15838 |  | 415839 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15838_U3_number_of_strings_on_branch_3_count |  | This point is not mapped to ignition
1014 | Available | Holding Register | U3 number of strings on branch 4 | 16-bit unsigned integer | 15839 |  | 415840 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15839_U3_number_of_strings_on_branch_4_count |  | This point is not mapped to ignition
1015 | Available | Holding Register | U3 number of strings on branch 5 | 16-bit unsigned integer | 15840 |  | 415841 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15840_U3_number_of_strings_on_branch_5_count |  | This point is not mapped to ignition
1016 | Available | Holding Register | U3 number of strings on branch 6 | 16-bit unsigned integer | 15841 |  | 415842 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15841_U3_number_of_strings_on_branch_6_count |  | This point is not mapped to ignition
1017 | Available | Holding Register | U3 number of strings on branch 7 | 16-bit unsigned integer | 15842 |  | 415843 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15842_U3_number_of_strings_on_branch_7_count |  | This point is not mapped to ignition
1018 | Available | Holding Register | U4 number of strings on branch 1 | 16-bit unsigned integer | 15852 |  | 415853 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15852_U4_number_of_strings_on_branch_1_count |  | This point is not mapped to ignition
1019 | Available | Holding Register | U4 number of strings on branch 2 | 16-bit unsigned integer | 15853 |  | 415854 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15853_U4_number_of_strings_on_branch_2_count |  | This point is not mapped to ignition
1020 | Available | Holding Register | U4 number of strings on branch 3 | 16-bit unsigned integer | 15854 |  | 415855 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15854_U4_number_of_strings_on_branch_3_count |  | This point is not mapped to ignition
1021 | Available | Holding Register | U4 number of strings on branch 4 | 16-bit unsigned integer | 15855 |  | 415856 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15855_U4_number_of_strings_on_branch_4_count |  | This point is not mapped to ignition
1022 | Available | Holding Register | U4 number of strings on branch 5 | 16-bit unsigned integer | 15856 |  | 415857 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15856_U4_number_of_strings_on_branch_5_count |  | This point is not mapped to ignition
1023 | Available | Holding Register | U4 number of strings on branch 6 | 16-bit unsigned integer | 15857 |  | 415858 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15857_U4_number_of_strings_on_branch_6_count |  | This point is not mapped to ignition
1024 | Available | Holding Register | U4 number of strings on branch 7 | 16-bit unsigned integer | 15858 |  | 415859 |  |  |  |  | count | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_15858_U4_number_of_strings_on_branch_7_count |  | This point is not mapped to ignition
Note on S6: Format: (Low-Low,Low,High,High-High)
Note on B749: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B750: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B751: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B752: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B753: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B754: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B755: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on B756: Josh Walker: These registers require optional instruments. Sunlight Road is not equipped with the option
Note on X757: Zone Monitor Work State: 0: Disable 1: Self-Study 2: Fault Detection
Note on X858: Start Stop Enumeration: 16#CE - Start 16#CF - Stop All others no operation
Note on X859: Start Stop Enumeration: 16#CE - Emergency Stop All others no operation
Note on X861: Local/Remote Control: 0 - Remote control 1 - Local control
Note on X862: Reactive Power Mode: 16#55 - OFF 16#A1 - Power factor mode 16#A2 - Reactive output mode 16#A3 - QU mode 16#A5 - QP mode
Note on X871: Start Stop Enumeration: 16#CE - Off? 16#CF - On? All others no operation Need to confirm
Note on X872: Start Stop Enumeration: 16#CE - Off? 16#CF - On? All others no operation Need to confirm
Note on X873: Start Stop Enumeration: 16#CE - Off? 16#CF - On? All others no operation Need to confirm
Note on X874: Start Stop Enumeration: 16#CE - Off? 16#CF - On? All others no operation Need to confirm
Note on X879: QU Operation Mode: 16#A1 - Reactive power ratio mode 16#A2 - Active power ratio mode 16#A3 - Power factor mode
Note on X880: Voltage Source: 16#B1 - real time voltage 16#B2 - record voltage
Note on X889: Junior Metayer: 0: Open 1: Close
Note on X892: Enable Disable P(U): 16#55 - Disable 16#AA - Enable
Note on X895: DC Switch Open/Close: 16#55 - Close 16#AA - Open
Note on X896: Night SVG Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X902: Frequency modulation Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X907: Frequency Source: 16#B1 - real time frequency 16#B2 - record frequency
Note on X960: Active Power Closed Loop Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X961: Reactive Power Closed Loop Enable/Disable: 16#55 - Disable 16#AA - Enable
Note on X962: Junior Metayer: 16#A1: rated power 16#A2: power before derating 16#A3: maximum power 16#A4: Pmax-Pm
Note on X963: Junior Metayer: 16#A1: rated power 16#A2: power before derating 16#A3: maximum power 16#A4: Pmax-Pm
Note on X971: Frequency output change benchmark: 16#A1 - function u nknown 16#A2 - function unknown
Note on X979: Junior Metayer: 0: Disable 1: Enable
Note on X980: Junior Metayer: 0: Disable 1: Enable

## Met Tower to PPC
Site Name | [5 empty] | Modbus |  |  |  | Met Tower to PPC
Last updated |  | 2023-06-05 | Device Type | Groundwork Zenith | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Environmental
Device Register Base |  | 1
Register Digits |  | 5
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Holding Register | Scan count | 32-bit float | 0 |  | 40001 |  |  |  |  | s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0000_Scan_count_s
2 | Available | Holding Register | Skipped scans | 32-bit float | 2 |  | 40003 |  |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0002_Skipped_scans_count
3 | Available | Holding Register | Logger voltage | 32-bit float | 4 |  | 40005 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0004_Logger_voltage_V
4 | Available | Holding Register | Logger temp | 32-bit float | 6 |  | 40007 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0006_Logger_temp_DegC
5 | Available | Holding Register | Skipped slow scans | 32-bit float | 8 |  | 40009 |  |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0008_Skipped_slow_scans_count
6 | Available | Holding Register | Logger lithium | 32-bit float | 10 |  | 40011 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0010_Logger_lithium_V
7 | Available | Holding Register | Logger low volt 12 | 32-bit float | 12 |  | 40013 |  |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0012_Logger_low_volt_12_count
8 | Available | Holding Register | Solar zenith | 32-bit float | 16 |  | 40017 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0016_Solar_zenith_degrees
9 | Available | Holding Register | Solar elevation | 32-bit float | 18 |  | 40019 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0018_Solar_elevation_degrees
10 | Available | Holding Register | Solar azimuth | 32-bit float | 20 |  | 40021 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0020_Solar_azimuth_degrees
11 | Available | Holding Register | Heat state | 32-bit float | 22 |  | 40023 |  |  | On | Off | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0022_Heat_state_boolean
12 | Available | Holding Register | Logger data map version | 32-bit float | 24 |  | 40025 |  |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0024_Logger_data_map_version
13 | Available | Holding Register | Maint event | 32-bit float | 26 |  | 40027 |  |  | On | Off | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0026_Maint_event_boolean
14 | Available | Holding Register | Logger AC power available | 32-bit float | 28 |  | 40029 |  |  | On | Off | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0028_Logger_AC_power_available_boolean | 0 to 1
15 | Available | Holding Register | Batt voltage | 32-bit float | 30 |  | 40031 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0030_Batt_voltage_V
16 | Available | Holding Register | Batt current | 32-bit float | 32 |  | 40033 |  |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0032_Batt_current_A
17 | Available | Holding Register | Load current | 32-bit float | 34 |  | 40035 |  |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0034_Load_current_A
18 | Available | Holding Register | Input voltage 1 | 32-bit float | 36 |  | 40037 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0036_Input_voltage_1_V
19 | Available | Holding Register | Chargesource | 32-bit float | 40 |  | 40041 |  |  |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0040_Chargesource |  | 0 = None, 1 = Solar, 2 = AC Power
20 | Available | Holding Register | Checkbattery | 32-bit float | 42 |  | 40043 |  |  | Alarm | Alarm | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0042_Checkbattery
21 | Available | Holding Register | Input voltage 2 | 32-bit float | 44 |  | 40045 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0044_Input_voltage_2_V
22 | Available | Holding Register | POA | 32-bit float | 46 |  | 40047 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0046_POA_W_per_m2
23 | Available | Holding Register | POA temperature compensated | 32-bit float | 48 |  | 40049 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0048_POA_temperature_compensated_W_per_m2
24 | Available | Holding Register | POA temp | 32-bit float | 50 |  | 40051 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0050_POA_temp_DegC
25 | Available | Holding Register | GHI | 32-bit float | 52 |  | 40053 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0052_GHI_W_per_m2
26 | Available | Holding Register | GHI temperature compensated | 32-bit float | 54 |  | 40055 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0054_GHI_temperature_compensated_W_per_m2
27 | Available | Holding Register | GHI temp | 32-bit float | 56 |  | 40057 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0056_GHI_temp_DegC
28 | Available | Holding Register | Ambient temp | 32-bit float | 74 |  | 40075 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0074_Ambient_temp_DegC
29 | Available | Holding Register | Dew point | 32-bit float | 76 |  | 40077 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0076_Dew_point_DegC
30 | Available | Holding Register | RH | 32-bit float | 78 |  | 40079 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0078_RH_pct
31 | Available | Holding Register | Wind speed | 32-bit float | 80 |  | 40081 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0080_Wind_speed_m_per_s
32 | Available | Holding Register | Wind speed max | 32-bit float | 82 |  | 40083 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0082_Wind_speed_max_m_per_s
33 | Available | Holding Register | Wind dir | 32-bit float | 84 |  | 40085 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0084_Wind_dir_degrees
34 | Available | Holding Register | Wsxxx wind quality | 32-bit float | 86 |  | 40087 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0086_Wsxxx_wind_quality_pct
35 | Available | Holding Register | BP | 32-bit float | 88 |  | 40089 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0088_BP_mbar
36 | Available | Holding Register | BP sea level | 32-bit float | 90 |  | 40091 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0090_BP_sea_level_mbar
37 | Available | Holding Register | Wsxxx compass | 32-bit float | 92 |  | 40093 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0092_Wsxxx_compass_degrees
38 | Available | Holding Register | Wind chill | 32-bit float | 94 |  | 40095 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0094_Wind_chill_DegC
39 | Available | Holding Register | Heat index | 32-bit float | 96 |  | 40097 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0096_Heat_index_DegC
40 | Available | Holding Register | Rain instantaneous | 32-bit float | 104 |  | 40105 |  |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0104_Rain_instantaneous_mm
41 | Available | Holding Register | Rain intensity | 32-bit float | 106 |  | 40107 |  |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0106_Rain_intensity_mm_per_hr
42 | Available | Holding Register | Rain today | 32-bit float | 108 |  | 40109 |  |  |  |  | mm/day | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0108_Rain_today_mm_per_day
43 | Available | Holding Register | BOM temp 1 | 32-bit float | 124 |  | 40125 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0124_BOM_temp_1_DegC
44 | Available | Holding Register | BOM temp 2 | 32-bit float | 126 |  | 40127 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0126_BOM_temp_2_DegC
45 | Available | Holding Register | BOM temp 3 | 32-bit float | 128 |  | 40129 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0128_BOM_temp_3_DegC
46 | Available | Holding Register | POA insolation | 32-bit float | 174 |  | 40175 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0174_POA_insolation_Wh_per_m²
47 | Available | Holding Register | GHI insolation | 32-bit float | 176 |  | 40177 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0176_GHI_insolation_Wh_per_m²
48 | Available | Holding Register | Hourly POA avg | 32-bit float | 198 |  | 40199 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0198_Hourly_POA_avg_W_per_m2
49 | Available | Holding Register | Hourly POA temperature compensated avg | 32-bit float | 200 |  | 40201 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0200_Hourly_POA_temperature_compensated_avg_W_per_m2
50 | Available | Holding Register | Hourly POA temp avg | 32-bit float | 202 |  | 40203 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0202_Hourly_POA_temp_avg_DegC
51 | Available | Holding Register | Hourly GHI avg | 32-bit float | 204 |  | 40205 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0204_Hourly_GHI_avg_W_per_m2
52 | Available | Holding Register | Hourly GHI temperature compensated avg | 32-bit float | 206 |  | 40207 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0206_Hourly_GHI_temperature_compensated_avg_W_per_m2
53 | Available | Holding Register | Hourly GHI temp avg | 32-bit float | 208 |  | 40209 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0208_Hourly_GHI_temp_avg_DegC
54 | Available | Holding Register | Hourly ambient temp avg | 32-bit float | 226 |  | 40227 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0226_Hourly_ambient_temp_avg_DegC
55 | Available | Holding Register | Hourly dew point avg | 32-bit float | 228 |  | 40229 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0228_Hourly_dew_point_avg_DegC
56 | Available | Holding Register | Hourly RH | 32-bit float | 230 |  | 40231 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0230_Hourly_RH_pct
57 | Available | Holding Register | Hourly wind speed mean | 32-bit float | 232 |  | 40233 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0232_Hourly_wind_speed_mean_m_per_s
58 | Available | Holding Register | Hourly wind speed max | 32-bit float | 234 |  | 40235 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0234_Hourly_wind_speed_max_m_per_s
59 | Available | Holding Register | Hourly wind dir mean | 32-bit float | 236 |  | 40237 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0236_Hourly_wind_dir_mean_Degrees
60 | Available | Holding Register | Hourly BP avg | 32-bit float | 238 |  | 40239 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0238_Hourly_BP_avg_mbar
61 | Available | Holding Register | Hourly BP sea level avg | 32-bit float | 240 |  | 40241 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0240_Hourly_BP_sea_level_avg_mbar
62 | Available | Holding Register | Hourly wsxxx compass | 32-bit float | 242 |  | 40243 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0242_Hourly_wsxxx_compass_degrees
63 | Available | Holding Register | Hourly wind chill avg | 32-bit float | 244 |  | 40245 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0244_Hourly_wind_chill_avg_DegC
64 | Available | Holding Register | Hourly heat index avg | 32-bit float | 246 |  | 40247 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0246_Hourly_heat_index_avg_DegC
65 | Available | Holding Register | Hourly rain instantaneous tot | 32-bit float | 254 |  | 40255 |  |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0254_Hourly_rain_instantaneous_tot_mm
66 | Available | Holding Register | Hourly rain intensity avg | 32-bit float | 256 |  | 40257 |  |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0256_Hourly_rain_intensity_avg_mm_per_hr
67 | Available | Holding Register | Hourly rain intensity max | 32-bit float | 258 |  | 40259 |  |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0258_Hourly_rain_intensity_max_mm_per_hr
68 | Available | Holding Register | Hourly BOM temp 1 avg | 32-bit float | 274 |  | 40275 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0274_Hourly_BOM_temp_1_avg_DegC
69 | Available | Holding Register | Hourly BOM temp 2 avg | 32-bit float | 276 |  | 40277 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0276_Hourly_BOM_temp_2_avg_DegC
70 | Available | Holding Register | Hourly BOM temp 3 avg | 32-bit float | 278 |  | 40279 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0278_Hourly_BOM_temp_3_avg_DegC
71 | Available | Holding Register | Hourly POA insolation tot | 32-bit float | 324 |  | 40325 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0324_Hourly_POA_insolation_tot_Wh_per_m²
72 | Available | Holding Register | Hourly GHI insolation tot | 32-bit float | 326 |  | 40327 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0326_Hourly_GHI_insolation_tot_Wh_per_m²
73 | Available | Holding Register | POA humidity | 32-bit float | 350 |  | 40351 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0350_POA_humidity_pct
74 | Available | Holding Register | POA humidity temp | 32-bit float | 352 |  | 40353 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0352_POA_humidity_temp_DegC
75 | Available | Holding Register | POA tilt | 32-bit float | 354 |  | 40355 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0354_POA_tilt_Degrees
76 | Available | Holding Register | POA fan speed | 32-bit float | 356 |  | 40357 |  |  |  |  | RPM | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0356_POA_fan_speed_RPM
77 | Available | Holding Register | POA heat current | 32-bit float | 358 |  | 40359 |  |  |  |  | mA | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0358_POA_heat_current_mA
78 | Available | Holding Register | GHI humidity | 32-bit float | 362 |  | 40363 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0362_GHI_humidity_pct
79 | Available | Holding Register | GHI humidity temp | 32-bit float | 364 |  | 40365 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0364_GHI_humidity_temp_DegC
80 | Available | Holding Register | GHI tilt | 32-bit float | 366 |  | 40367 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0366_GHI_tilt_Degrees
81 | Available | Holding Register | GHI fan speed | 32-bit float | 368 |  | 40369 |  |  |  |  | RPM | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0368_GHI_fan_speed_RPM
82 | Available | Holding Register | GHI heat current | 32-bit float | 370 |  | 40371 |  |  |  |  | mA | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0370_GHI_heat_current_mA
83 | Available | Holding Register | Logger temp | 32-bit float | 404 |  | 40405 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0404_Logger_temp_DegF
84 | Available | Holding Register | Ambient temp f | 32-bit float | 472 |  | 40473 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0472_Ambient_temp_f_DegF
85 | Available | Holding Register | Dew point | 32-bit float | 474 |  | 40475 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0474_Dew_point_DegF
86 | Available | Holding Register | Wind speed | 32-bit float | 478 |  | 40479 |  |  |  |  | mph | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0478_Wind_speed_mph
87 | Available | Holding Register | Wind speed max | 32-bit float | 480 |  | 40481 |  |  |  |  | mph | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0480_Wind_speed_max_mph
88 | Available | Holding Register | BP hg | 32-bit float | 486 |  | 40487 |  |  |  |  | inHg | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0486_BP_hg_inHg
89 | Available | Holding Register | BP sea level hg | 32-bit float | 488 |  | 40489 |  |  |  |  | inHg | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0488_BP_sea_level_hg_inHg
90 | Available | Holding Register | Rain instantaneous | 32-bit float | 502 |  | 40503 |  |  |  |  | in | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0502_Rain_instantaneous_in
91 | Available | Holding Register | Rain intensity | 32-bit float | 504 |  | 40505 |  |  |  |  | in/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0504_Rain_intensity_in_per_hr
92 | Available | Holding Register | Rain today | 32-bit float | 506 |  | 40507 |  |  |  |  | in/day | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0506_Rain_today_in_per_day
93 | Available | Holding Register | BOM temp 1 | 32-bit float | 522 |  | 40523 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0522_BOM_temp_1_DegF
94 | Available | Holding Register | BOM temp 2 | 32-bit float | 524 |  | 40525 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0524_BOM_temp_2_DegF
95 | Available | Holding Register | BOM temp 3 | 32-bit float | 526 |  | 40527 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0526_BOM_temp_3_DegF
96 | Available | Holding Register | RPOA irradiance | 32-bit float | 746 |  | 40747 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0746_RPOA_irradiance_W_per_m2
97 | Available | Holding Register | RPOA temperature corrected irradiance | 32-bit float | 748 |  | 40749 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0748_RPOA_temperature_corrected_irradiance_W_per_m2
98 | Available | Holding Register | RPOA case temp | 32-bit float | 750 |  | 40751 |  |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0750_RPOA_case_temp_degC
99 | Available | Holding Register | RPOA isolation | 32-bit float | 752 |  | 40753 |  |  |  |  | Wh/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0752_RPOA_isolation_Wh_per_m2
100 | Available | Holding Register | RPOA unit humidity | 32-bit float | 770 |  | 40771 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0770_RPOA_unit_humidity__pct
101 | Available | Holding Register | RPOA unit temp | 32-bit float | 772 |  | 40773 |  |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0772_RPOA_unit_temp__degC
102 | Available | Holding Register | RPOA unit tilt | 32-bit float | 774 |  | 40775 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0774_RPOA_unit_tilt_degrees
103 | Available | Holding Register | RPOA unit fan speed | 32-bit float | 776 |  | 40777 |  |  |  |  | rpm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0776_RPOA_unit_fan_speed_rpm
104 | Available | Holding Register | Modeled GHI | 32-bit float | 798 |  | 40799 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0798_Modeled_GHI_W_per_m2
105 | Available | Holding Register | Modeled DHI | 32-bit float | 800 |  | 40801 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0800_Modeled_DHI_W_per_m2
106 | Available | Holding Register | Modeled DNI | 32-bit float | 802 |  | 40803 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0802_Modeled_DNI_W_per_m2
107 | Available | Holding Register | Modeled POA | 32-bit float | 803 |  | 40804 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0803_Modeled_POA_W_per_m2
108 | Available | Holding Register | RPOA hourly irradiance | 32-bit float | 838 |  | 40839 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0838_RPOA_hourly_irradiance_W_per_m2
109 | Available | Holding Register | RPOA hourly temperature corrected irradiance | 32-bit float | 840 |  | 40841 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0840_RPOA_hourly_temperature_corrected_irradiance_W_per_m2
110 | Available | Holding Register | RPOA hourly case temp | 32-bit float | 842 |  | 40843 |  |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0842_RPOA_hourly_case_temp_degC
111 | Available | Holding Register | RPOA hourly insolation | 32-bit float | 844 |  | 40845 |  |  |  |  | Wh/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0844_RPOA_hourly_insolation_Wh_per_m2
99 | Available | Holding Register | Summary alarm | 32-bit unsigned int | 2000 |  | 42001 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2000_Summary_alarm
100 | Available | Holding Register | Data logger alarms register | 32-bit unsigned int | 2002 |  | 42003 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2002_Data_logger_alarms_register
101 | Available | Holding Register | Data logger watchdog error | Boolean | 2002 | 0 | 42003 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_watchdog_error
102 | Available | Holding Register | Data logger skipped main scan | Boolean | 2002 | 1 | 42003.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_skipped_main_scan
103 | Available | Holding Register | Data logger skipped slow scan | Boolean | 2002 | 2 | 42003.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_skipped_slow_scan
104 | Available | Holding Register | Data logger program variable out of bounds | Boolean | 2002 | 3 | 42003.3 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_program_variable_out_of_bounds
105 | Available | Holding Register | Data logger low 12V | Boolean | 2002 | 4 | 42003.4 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_12V
106 | Available | Holding Register | Data logger low 5V | Boolean | 2002 | 5 | 42003.5 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_5V
107 | Available | Holding Register | Data logger lithium battery error | Boolean | 2002 | 8 | 42003.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_lithium_battery_error
108 | Available | Holding Register | Data logger lithium battery low | Boolean | 2002 | 9 | 42003.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_lithium_battery_low
109 | Available | Holding Register | Data logger lithium battery critical | Boolean | 2002 | 10 | 42003.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_lithium_battery_critical
110 | Available | Holding Register | Data logger voltage error | Boolean | 2002 | 16 | 42003.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_voltage_error
111 | Available | Holding Register | Data logger low voltage warning | Boolean | 2002 | 17 | 42003.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_voltage_warning
112 | Available | Holding Register | Data logger low voltage | Boolean | 2002 | 18 | 42003.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_voltage
113 | Available | Holding Register | Data logger over voltage | Boolean | 2002 | 19 | 42003.19 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_over_voltage
114 | Available | Holding Register | Data logger temperature error | Boolean | 2002 | 24 | 42003.24 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_temperature_error
115 | Available | Holding Register | Data logger temperature below operating range | Boolean | 2002 | 25 | 42003.25 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_temperature_below_operating_range
116 | Available | Holding Register | Data logger temperature above operating range | Boolean | 2002 | 26 | 42003.26 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_temperature_above_operating_range
117 | Available | Holding Register | Battery alarms register | 32-bit unsigned int | 2004 |  | 42005 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2004_Battery_alarms_register
118 | Available | Holding Register | Check battery | Boolean | 2004 | 0 | 42005 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Check_battery
119 | Available | Holding Register | Battery voltage error | Boolean | 2004 | 8 | 42005.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Battery_voltage_error
120 | Available | Holding Register | Low battery voltage warning | Boolean | 2004 | 9 | 42005.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Low_battery_voltage_warning
121 | Available | Holding Register | Low battery voltage critical | Boolean | 2004 | 10 | 42005.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Low_battery_voltage_critical
122 | Available | Holding Register | Low battery voltage deep discharge | Boolean | 2004 | 11 | 42005.11 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Low_battery_voltage_deep_discharge
123 | Available | Holding Register | Battery current error | Boolean | 2004 | 16 | 42005.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Battery_current_error
124 | Available | Holding Register | Excessive battery current warning | Boolean | 2004 | 17 | 42005.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Excessive_battery_current_warning
125 | Available | Holding Register | Excessive battery current critical | Boolean | 2004 | 18 | 42005.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Excessive_battery_current_critical
126 | Available | Holding Register | Charging alarms register | 32-bit unsigned int | 2006 |  | 42007 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Charging_alarms_register
127 | Available | Holding Register | Input voltage error | Boolean | 2006 | 0 | 42007 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Input_voltage_error
128 | Available | Holding Register | Rpu enabled | Boolean | 2006 | 1 | 42007.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Rpu_enabled
129 | Available | Holding Register | Input current error | Boolean | 2006 | 8 | 42007.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Input_current_error
130 | Available | Holding Register | Excessive input current | Boolean | 2006 | 9 | 42007.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Excessive_input_current
131 | Available | Holding Register | Load current error | Boolean | 2006 | 16 | 42007.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Load_current_error
132 | Available | Holding Register | Excessive load current warning | Boolean | 2006 | 17 | 42007.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Excessive_load_current_warning
133 | Available | Holding Register | Excessive load current | Boolean | 2006 | 18 | 42007.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Excessive_load_current
134 | Available | Holding Register | GHI 1 alarms register | 32-bit unsigned int | 2018 |  | 42019 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2018_GHI_alarms_register
135 | Available | Holding Register | GHI 1 irradiance error | Boolean | 2018 | 0 | 42019 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_irradiance_error
136 | Available | Holding Register | GHI 1 irradiance negative | Boolean | 2018 | 1 | 42019.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_irradiance_negative
137 | Available | Holding Register | GHI 1 irradiance above solar constant | Boolean | 2018 | 2 | 42019.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_irradiance_above_solar_constant
138 | Available | Holding Register | GHI 1 temperature corrected irradiance error | Boolean | 2018 | 8 | 42019.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_temperature_corrected_irradiance_error
139 | Available | Holding Register | GHI 1 temperature corrected irradiance negative | Boolean | 2018 | 9 | 42019.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_temperature_corrected_irradiance_negative
140 | Available | Holding Register | GHI 1 temperature corrected irradiance above solar constant | Boolean | 2018 | 10 | 42019.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_temperature_corrected_irradiance_above_solar_constant
141 | Available | Holding Register | GHI 1 case temperature error | Boolean | 2018 | 16 | 42019.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_case_temperature_error
142 | Available | Holding Register | GHI 1 case temperature below operating range | Boolean | 2018 | 17 | 42019.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_case_temperature_below_operating_range
143 | Available | Holding Register | GHI 1 case temperature above operating range | Boolean | 2018 | 18 | 42019.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_case_temperature_above_operating_range
144 | Available | Holding Register | POA alarms register | 32-bit unsigned int | 2020 |  | 42021 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2020_POA_alarms_register
145 | Available | Holding Register | POA irradiance error | Boolean | 2020 | 0 | 42021 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_irradiance_error
146 | Available | Holding Register | POA irradiance negative | Boolean | 2020 | 1 | 42021.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_irradiance_negative
147 | Available | Holding Register | POA irradiance above solar constant | Boolean | 2020 | 2 | 42021.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_irradiance_above_solar_constant
148 | Available | Holding Register | POA temperature corrected irradiance error | Boolean | 2020 | 8 | 42021.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_temperature_corrected_irradiance_error
149 | Available | Holding Register | POA temperature corrected irradiance negative | Boolean | 2020 | 9 | 42021.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_temperature_corrected_irradiance_negative
150 | Available | Holding Register | POA temperature corrected irradiance above solar constant | Boolean | 2020 | 10 | 42021.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_temperature_corrected_irradiance_above_solar_constant
151 | Available | Holding Register | POA case temperature error | Boolean | 2020 | 16 | 42021.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_case_temperature_error
152 | Available | Holding Register | POA case temperature below operating range | Boolean | 2020 | 17 | 42021.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_case_temperature_below_operating_range
153 | Available | Holding Register | POA case temperature above operating range | Boolean | 2020 | 18 | 42021.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_case_temperature_above_operating_range
154 | Available | Holding Register | Multifunction alarms register | 32-bit unsigned int | 2038 |  | 42039 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2038_Multifunction_alarms_register
155 | Available | Holding Register | Ambient temperature error | Boolean | 2038 | 0 | 42039 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Ambient_temperature_error
156 | Available | Holding Register | Ambient temperature below operating range | Boolean | 2038 | 1 | 42039.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Ambient_temperature_below_operating_range
157 | Available | Holding Register | Ambient temperature above operating range | Boolean | 2038 | 2 | 42039.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Ambient_temperature_above_operating_range
158 | Available | Holding Register | Dew point error | Boolean | 2038 | 3 | 42039.3 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Dew_point_error
159 | Available | Holding Register | Dew point above ambient temperature | Boolean | 2038 | 4 | 42039.4 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Dew_point_above_ambient_temperature
160 | Available | Holding Register | Condensation warning | Boolean | 2038 | 5 | 42039.5 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Condensation_warning
161 | Available | Holding Register | Relative humidity error | Boolean | 2038 | 8 | 42039.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Relative_humidity_error
162 | Available | Holding Register | Relative humidity below operating range | Boolean | 2038 | 9 | 42039.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Relative_humidity_below_operating_range
163 | Available | Holding Register | Relative humidity above operating range | Boolean | 2038 | 10 | 42039.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Relative_humidity_above_operating_range
164 | Available | Holding Register | Absolute barometric pressure error | Boolean | 2038 | 16 | 42039.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Absolute_barometric_pressure_error
165 | Available | Holding Register | Absolute barometric pressure below operating range | Boolean | 2038 | 17 | 42039.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Absolute_barometric_pressure_below_operating_range
166 | Available | Holding Register | Absolute barometric pressure above operating range | Boolean | 2038 | 18 | 42039.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Absolute_barometric_pressure_above_operating_range
167 | Available | Holding Register | Sea level barometric pressure error | Boolean | 2038 | 24 | 42039.24 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Sea_level_barometric_pressure_error
168 | Available | Holding Register | Sea level barometric pressure below operating range | Boolean | 2038 | 25 | 42039.25 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Sea_level_barometric_pressure_below_operating_range
169 | Available | Holding Register | Sea level barometric pressure above operating range | Boolean | 2038 | 26 | 42039.26 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Sea_level_barometric_pressure_above_operating_range
170 | Available | Holding Register | Wind alarms register | 32-bit unsigned int | 2040 |  | 42041 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2040_Wind_alarms_register
171 | Available | Holding Register | Wind speed error | Boolean | 2040 | 0 | 42041 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_error
172 | Available | Holding Register | Wind speed below operating range | Boolean | 2040 | 1 | 42041.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_below_operating_range
173 | Available | Holding Register | Wind speed above operating range | Boolean | 2040 | 2 | 42041.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_above_operating_range
174 | Available | Holding Register | Wind speed unable to execute measurement due to ambient conditions | Boolean | 2040 | 3 | 42041.3 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_unable_to_execute_measurement_due_to_ambient_conditions
175 | Available | Holding Register | Wind speed quality warning | Boolean | 2040 | 4 | 42041.4 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_quality_warning
176 | Available | Holding Register | Wind speed quality error | Boolean | 2040 | 5 | 42041.5 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_quality_error
177 | Available | Holding Register | Wind speed max error | Boolean | 2040 | 8 | 42041.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_max_error
178 | Available | Holding Register | Wind speed max below operating range | Boolean | 2040 | 9 | 42041.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_max_below_operating_range
179 | Available | Holding Register | Wind speed max above operating range | Boolean | 2040 | 10 | 42041.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_max_above_operating_range
180 | Available | Holding Register | Wind direction error | Boolean | 2040 | 16 | 42041.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_direction_error
181 | Available | Holding Register | Wind direction below operating range | Boolean | 2040 | 17 | 42041.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_direction_below_operating_range
182 | Available | Holding Register | Wind direction above operating range | Boolean | 2040 | 18 | 42041.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_direction_above_operating_range
183 | Available | Holding Register | Compass error | Boolean | 2040 | 24 | 42041.24 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Compass_error
184 | Available | Holding Register | Compass below operating range | Boolean | 2040 | 25 | 42041.25 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Compass_below_operating_range
185 | Available | Holding Register | Compass above operating range | Boolean | 2040 | 26 | 42041.26 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Compass_above_operating_range
186 | Available | Holding Register | Rain alarms regsiter | 32-bit unsigned int | 2042 |  | 42043 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2042_Rain_alarms_regsiter
187 | Available | Holding Register | Rain total error | Boolean | 2042 | 0 | 42043 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_total_error
188 | Available | Holding Register | Rain total negative | Boolean | 2042 | 1 | 42043.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_total_negative
189 | Available | Holding Register | Rain total above operating range | Boolean | 2042 | 2 | 42043.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_total_above_operating_range
190 | Available | Holding Register | Rain intensity error | Boolean | 2042 | 8 | 42043.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_intensity_error
191 | Available | Holding Register | Rain intensity negative | Boolean | 2042 | 9 | 42043.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_intensity_negative
192 | Available | Holding Register | Rain intensity above operating range | Boolean | 2042 | 10 | 42043.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_intensity_above_operating_range
193 | Available | Holding Register | Rain today error | Boolean | 2042 | 16 | 42043.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_today_error
194 | Available | Holding Register | Rain today is negative | Boolean | 2042 | 17 | 42043.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_today_is_negative
195 | Available | Holding Register | Rain today above operating range | Boolean | 2042 | 18 | 42043.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_today_above_operating_range
196 | Available | Holding Register | GHI alarm register | 32-bit unsigned int | 2044 |  | 42045 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2044_GHI_alarm_register
197 | Available | Holding Register | Global irradiance error | Boolean | 2044 | 0 | 42045 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Global_irradiance_error
198 | Available | Holding Register | Global irradiance below operating range | Boolean | 2044 | 1 | 42045.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Global_irradiance_below_operating_range
199 | Available | Holding Register | Global irradiance above operating range | Boolean | 2044 | 2 | 42045.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Global_irradiance_above_operating_range
200 | Available | Holding Register | Diffuse irradiance error | Boolean | 2044 | 8 | 42045.8 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Diffuse_irradiance_error
201 | Available | Holding Register | Diffuse irradiance below operating range | Boolean | 2044 | 9 | 42045.9 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Diffuse_irradiance_below_operating_range
202 | Available | Holding Register | Diffuse irradiance above operating range | Boolean | 2044 | 10 | 42045.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Diffuse_irradiance_above_operating_range
203 | Available | Holding Register | Direct irradiance error | Boolean | 2044 | 16 | 42045.16 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Direct_irradiance_error
204 | Available | Holding Register | Direct irradiance below operating range | Boolean | 2044 | 17 | 42045.17 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Direct_irradiance_below_operating_range
205 | Available | Holding Register | Direct irradiance above operating range | Boolean | 2044 | 18 | 42045.18 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2044_Direct_irradiance_above_operating_range
206 | Available | Holding Register | BOM 1 alarm register | 32-bit unsigned int | 2058 |  | 42059 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2058_BOM_1_alarm_register
207 | Available | Holding Register | BOM 1 temperature error | Boolean | 2058 | 0 | 42059 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2058_BOM_1_temperature_error
208 | Available | Holding Register | BOM 1 temperature below operating range | Boolean | 2058 | 1 | 42059.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2058_BOM_1_temperature_below_operating_range
209 | Available | Holding Register | BOM 1 temperature above operating range | Boolean | 2058 | 2 | 42059.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2058_BOM_1_temperature_above_operating_range
210 | Available | Holding Register | BOM 2 alarm register | 32-bit unsigned int | 2060 |  | 42061 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2060_BOM_2_alarm_register
211 | Available | Holding Register | BOM 2 temperature error | Boolean | 2060 | 0 | 42061 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2060_BOM_2_temperature_error
212 | Available | Holding Register | BOM 2 temperature below operating range | Boolean | 2060 | 1 | 42061.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2060_BOM_2_temperature_below_operating_range
213 | Available | Holding Register | BOM 2 temperature above operating range | Boolean | 2060 | 2 | 42061.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2060_BOM_2_temperature_above_operating_range
214 | Available | Holding Register | BOM 3 alarm register | 32-bit unsigned int | 2062 |  | 42063 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2062_BOM_3_alarm_register
215 | Available | Holding Register | BOM 3 temperature error | Boolean | 2062 | 0 | 42063 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2062_BOM_3_temperature_error
216 | Available | Holding Register | BOM 3 temperature below operating range | Boolean | 2062 | 1 | 42063.1 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2062_BOM_3_temperature_below_operating_range
217 | Available | Holding Register | BOM 3 temperature above operating range | Boolean | 2062 | 2 | 42063.2 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2062_BOM_3_temperature_above_operating_range
Note on S6: Format: (Low-Low,Low,High,High-High)

## Met Tower ALB to Ignition
Speedway | [5 empty] | Modbus |  |  |  | Met Tower with Albedometer to Ignition
Last updated |  | 2025-01-26 | Device Type | Groundwork Zenith | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Environmental
Device Register Base |  | 1
Register Digits |  | 5
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Holding Register | Scan count | 32-bit float | 0 |  | 40001 |  |  |  |  | s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0000_Scan_count_s
2 | Available | Holding Register | Skipped scans | 32-bit float | 2 |  | 40002 |  |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0002_Skipped_scans_count
3 | Available | Holding Register | Logger voltage | 32-bit float | 4 |  | 40003 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0004_Logger_voltage_V
4 | Available | Holding Register | Logger temp | 32-bit float | 6 |  | 40004 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0006_Logger_temp_DegC
5 | Available | Holding Register | Skipped slow scans | 32-bit float | 8 |  | 40005 |  |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0008_Skipped_slow_scans_count
6 | Available | Holding Register | Logger lithium | 32-bit float | 10 |  | 40006 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0010_Logger_lithium_V
7 | Available | Holding Register | Logger low volt 12 | 32-bit float | 12 |  | 40007 |  |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0012_Logger_low_volt_12_count
8 | Available | Holding Register | Solar zenith | 32-bit float | 16 |  | 40008 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0016_Solar_zenith_degrees
9 | Available | Holding Register | Solar elevation | 32-bit float | 18 |  | 40009 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0018_Solar_elevation_degrees
10 | Available | Holding Register | Solar azimuth | 32-bit float | 20 |  | 40010 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0020_Solar_azimuth_degrees
11 | Available | Holding Register | Heat state | 32-bit float | 22 |  | 40011 |  |  | On | Off | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0022_Heat_state_boolean
12 | Available | Holding Register | Logger data map version | 32-bit float | 24 |  | 40012 |  |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0024_Logger_data_map_version
13 | Available | Holding Register | Maint event | 32-bit float | 26 |  | 40013 |  |  | On | Off | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0026_Maint_event_boolean
14 |  | Holding Register | Logger AC power | 32-bit float | 28 |  | 40014 |  |  | On | Off | boolean | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0028_Logger_AC_power_boolean
15 | Available | Holding Register | Batt voltage | 32-bit float | 30 |  | 40015 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0030_Batt_voltage_V
16 | Available | Holding Register | Batt current | 32-bit float | 32 |  | 40016 |  |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0032_Batt_current_A
17 | Available | Holding Register | Load current | 32-bit float | 34 |  | 40017 |  |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0034_Load_current_A
18 | Available | Holding Register | Input voltage 1 | 32-bit float | 36 |  | 40018 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0036_Input_voltage_1_V
19 | Available | Holding Register | Input current | 32-bit float | 38 |  | 40019 |  |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0038_Input_current_A
20 | Available | Holding Register | Chargesource | 32-bit float | 40 |  | 40020 |  |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0040_Chargesource
21 | Available | Holding Register | Checkbattery | 32-bit float | 42 |  | 40021 |  |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0042_Checkbattery
22 | Available | Holding Register | Input voltage 2 | 32-bit float | 44 |  | 40022 |  |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0044_Input_voltage_2_V
23 | Available | Holding Register | POA | 32-bit float | 46 |  | 40023 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0046_POA_W_per_m2
24 | Available | Holding Register | POA temperature compensated | 32-bit float | 48 |  | 40024 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0048_POA_temperature_compensated_W_per_m2
25 | Available | Holding Register | POA temp | 32-bit float | 50 |  | 40025 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0050_POA_temp_DegC
26 | Available | Holding Register | GHI 1 | 32-bit float | 52 |  | 40026 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0052_GHI_1_W_per_m2
27 | Available | Holding Register | GHI 1 temperature compensated | 32-bit float | 54 |  | 40027 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0054_GHI_1_temperature_compensated_W_per_m2
28 | Available | Holding Register | GHI 1 temp | 32-bit float | 56 |  | 40028 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0056_GHI_1_temp_DegC
29 | Available | Holding Register | GHI 2 | 32-bit float | 64 |  | 40029 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0064_GHI_2_W_per_m2
30 | Available | Holding Register | GHI 2 temperature compensated | 32-bit float | 66 |  | 40030 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0066_GHI_2_temperature_compensated_W_per_m2
31 | Available | Holding Register | GHI 2 temp | 32-bit float | 68 |  | 40031 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0068_GHI_2_temp_DegC
32 | Available | Holding Register | Ambient temp | 32-bit float | 74 |  | 40032 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0074_Ambient_temp_DegC
33 | Available | Holding Register | Dew point | 32-bit float | 76 |  | 40033 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0076_Dew_point_DegC
34 | Available | Holding Register | Relative humidity | 32-bit float | 78 |  | 40034 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0078_Relative_humidity_pct
35 | Available | Holding Register | Wind speed | 32-bit float | 80 |  | 40035 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0080_Wind_speed_m_per_s
36 | Available | Holding Register | Wind speed max | 32-bit float | 82 |  | 40036 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0082_Wind_speed_max_m_per_s
37 | Available | Holding Register | Wind direction | 32-bit float | 84 |  | 40037 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0084_Wind_direction_degrees
38 | Available | Holding Register | Wind measurement quality | 32-bit float | 86 |  | 40038 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0086_Wind_measurement_quality_pct
39 | Available | Holding Register | Barometric pressure | 32-bit float | 88 |  | 40039 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0088_Barometric_pressure_mbar
40 | Available | Holding Register | Barometric pressure at sea level | 32-bit float | 90 |  | 40040 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0090_Barometric_pressure_at_sea_level_mbar
41 | Available | Holding Register | Internal compass reading | 32-bit float | 92 |  | 40041 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0092_Internal_compass_reading_degrees
42 | Available | Holding Register | Wind chill | 32-bit float | 94 |  | 40042 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0094_Wind_chill_DegC
43 | Available | Holding Register | Heat index | 32-bit float | 96 |  | 40043 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0096_Heat_index_DegC
44 | Available | Holding Register | Rain instantaneous | 32-bit float | 104 |  | 40044 |  |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0104_Rain_instantaneous_mm
45 | Available | Holding Register | Rain intensity | 32-bit float | 106 |  | 40045 |  |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0106_Rain_intensity_mm_per_hr
46 | Available | Holding Register | Rain today | 32-bit float | 108 |  | 40046 |  |  |  |  | mm/day | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0108_Rain_today_mm_per_day
47 | Available | Holding Register | BOM temp 1 | 32-bit float | 124 |  | 40047 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0124_BOM_temp_1_DegC
48 | Available | Holding Register | BOM temp 2 | 32-bit float | 126 |  | 40048 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0126_BOM_temp_2_DegC
49 | Available | Holding Register | BOM temp 3 | 32-bit float | 128 |  | 40049 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0128_BOM_temp_3_DegC
50 | Available | Holding Register | POA insolation | 32-bit float | 174 |  | 40050 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0174_POA_insolation_Wh_per_m²
51 | Available | Holding Register | GHI insolation 1 | 32-bit float | 176 |  | 40051 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0176_GHI_insolation_1_Wh_per_m²
52 | Available | Holding Register | GHI insolation 2 | 32-bit float | 180 |  | 40052 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0180_GHI_insolation_2_Wh_per_m²
53 | Available | Holding Register | Hourly POA avg | 32-bit float | 198 |  | 40053 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0198_Hourly_POA_avg_W_per_m2
54 | Available | Holding Register | Hourly POA temperature compensated avg | 32-bit float | 200 |  | 40054 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0200_Hourly_POA_temperature_compensated_avg_W_per_m2
55 | Available | Holding Register | Hourly POA temp avg | 32-bit float | 202 |  | 40055 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0202_Hourly_POA_temp_avg_DegC
56 | Available | Holding Register | Hourly GHI 1 avg | 32-bit float | 204 |  | 40056 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0204_Hourly_GHI_1_avg_W_per_m2
57 | Available | Holding Register | Hourly GHI 1 temperature compensated avg | 32-bit float | 206 |  | 40057 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0206_Hourly_GHI_1_temperature_compensated_avg_W_per_m2
58 | Available | Holding Register | Hourly GHI 1 temp avg | 32-bit float | 208 |  | 40058 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0208_Hourly_GHI_1_temp_avg_DegC
59 | Available | Holding Register | Hourly GHI 2 avg | 32-bit float | 216 |  | 40059 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0216_Hourly_GHI_2_avg_W_per_m2
60 | Available | Holding Register | Hourly GHI 2 temperature compensated avg | 32-bit float | 218 |  | 40060 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0218_Hourly_GHI_2_temperature_compensated_avg_W_per_m2
61 | Available | Holding Register | Hourly GHI 2 temp avg | 32-bit float | 220 |  | 40061 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0220_Hourly_GHI_2_temp_avg_DegC
62 | Available | Holding Register | Hourly ambient temp avg | 32-bit float | 226 |  | 40062 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0226_Hourly_ambient_temp_avg_DegC
63 | Available | Holding Register | Hourly dew point avg | 32-bit float | 228 |  | 40063 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0228_Hourly_dew_point_avg_DegC
64 | Available | Holding Register | Hourly relative humidity | 32-bit float | 230 |  | 40064 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0230_Hourly_relative_humidity_pct
65 | Available | Holding Register | Hourly wind speed mean | 32-bit float | 232 |  | 40065 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0232_Hourly_wind_speed_mean_m_per_s
66 | Available | Holding Register | Hourly wind speed max | 32-bit float | 234 |  | 40066 |  |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0234_Hourly_wind_speed_max_m_per_s
67 | Available | Holding Register | Hourly wind direction mean | 32-bit float | 236 |  | 40067 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0236_Hourly_wind_direction_mean_Degrees
68 | Available | Holding Register | Hourly barometric pressure avg | 32-bit float | 238 |  | 40068 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0238_Hourly_barometric_pressure_avg_mbar
69 | Available | Holding Register | Hourly BP sea level avg | 32-bit float | 240 |  | 40069 |  |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0240_Hourly_BP_sea_level_avg_mbar
70 | Available | Holding Register | Hourly compass reading | 32-bit float | 242 |  | 40070 |  |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0242_Hourly_compass_reading_degrees
71 | Available | Holding Register | Hourly wind chill avg | 32-bit float | 244 |  | 40071 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0244_Hourly_wind_chill_avg_DegC
72 | Available | Holding Register | Hourly heat index avg | 32-bit float | 246 |  | 40072 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0246_Hourly_heat_index_avg_DegC
73 | Available | Holding Register | Hourly rain instantaneous tot | 32-bit float | 254 |  | 40073 |  |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0254_Hourly_rain_instantaneous_tot_mm
74 | Available | Holding Register | Hourly rain intensity avg | 32-bit float | 256 |  | 40074 |  |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0256_Hourly_rain_intensity_avg_mm_per_hr
75 | Available | Holding Register | Hourly rain intensity max | 32-bit float | 258 |  | 40075 |  |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0258_Hourly_rain_intensity_max_mm_per_hr
76 | Available | Holding Register | Hourly BOM temp 1 avg | 32-bit float | 274 |  | 40076 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0274_Hourly_BOM_temp_1_avg_DegC
77 | Available | Holding Register | Hourly BOM temp 2 avg | 32-bit float | 276 |  | 40077 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0276_Hourly_BOM_temp_2_avg_DegC
78 | Available | Holding Register | Hourly BOM temp 3 avg | 32-bit float | 278 |  | 40078 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0278_Hourly_BOM_temp_3_avg_DegC
79 | Available | Holding Register | Hourly POA insolation tot | 32-bit float | 324 |  | 40079 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0324_Hourly_POA_insolation_tot_Wh_per_m²
80 | Available | Holding Register | Hourly GHI insolation 1 tot | 32-bit float | 326 |  | 40080 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0326_Hourly_GHI_insolation_1_tot_Wh_per_m²
81 | Available | Holding Register | Hourly GHI insolation 2 tot | 32-bit float | 330 |  | 40081 |  |  |  |  | Wh/m² | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0330_Hourly_GHI_insolation_2_tot_Wh_per_m²
82 | Available | Holding Register | POA humidity | 32-bit float | 350 |  | 40082 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0350_POA_humidity_pct
83 | Available | Holding Register | POA humidity temp | 32-bit float | 352 |  | 40083 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0352_POA_humidity_temp_DegC
84 | Available | Holding Register | POA tilt | 32-bit float | 354 |  | 40084 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0354_POA_tilt_Degrees
85 | Available | Holding Register | POA fan speed | 32-bit float | 356 |  | 40085 |  |  |  |  | RPM | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0356_POA_fan_speed_RPM
86 | Available | Holding Register | POA heat current | 32-bit float | 358 |  | 40086 |  |  |  |  | A | 0.001 | -3.4028e+38 | 3.4028e+38 | -3.4028e+41 | 3.4028e+41 |  |  |  |  | HREG_0358_POA_heat_current_A
87 | Available | Holding Register | GHI humidity 1 | 32-bit float | 362 |  | 40087 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0362_GHI_humidity_1_pct
88 | Available | Holding Register | GHI humidity temp 1 | 32-bit float | 364 |  | 40088 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0364_GHI_humidity_temp_1_DegC
89 | Available | Holding Register | GHI tilt 1 | 32-bit float | 366 |  | 40089 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0366_GHI_tilt_1_Degrees
90 | Available | Holding Register | GHI fan speed 1 | 32-bit float | 368 |  | 40090 |  |  |  |  | RPM | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0368_GHI_fan_speed_1_RPM
91 | Available | Holding Register | GHI heat current 1 | 32-bit float | 370 |  | 40091 |  |  |  |  | A | 0.001 | -3.4028e+38 | 3.4028e+38 | -3.4028e+41 | 3.4028e+41 |  |  |  |  | HREG_0370_GHI_heat_current_1_A
92 | Available | Holding Register | GHI humidity 2 | 32-bit float | 386 |  | 40092 |  |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0386_GHI_humidity_2_pct
93 | Available | Holding Register | GHI humidity temp 2 | 32-bit float | 388 |  | 40093 |  |  |  |  | DegC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0388_GHI_humidity_temp_2_DegC
94 | Available | Holding Register | GHI tilt 2 | 32-bit float | 390 |  | 40094 |  |  |  |  | Degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0390_GHI_tilt_2_Degrees
95 | Available | Holding Register | GHI fan speed 2 | 32-bit float | 392 |  | 40095 |  |  |  |  | RPM | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0392_GHI_fan_speed_2_RPM
96 | Available | Holding Register | GHI heat current 2 | 32-bit float | 394 |  | 40096 |  |  |  |  | A | 0.001 | -3.4028e+38 | 3.4028e+38 | -3.4028e+41 | 3.4028e+41 |  |  |  |  | HREG_0394_GHI_heat_current_2_A
97 | Available | Holding Register | Logger temp | 32-bit float | 404 |  | 40097 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0404_Logger_temp_DegF
98 | Available | Holding Register | Ambient temp f | 32-bit float | 472 |  | 40098 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0472_Ambient_temp_f_DegF
99 | Available | Holding Register | Dew point | 32-bit float | 474 |  | 40099 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0474_Dew_point_DegF
100 | Available | Holding Register | Wind speed | 32-bit float | 478 |  | 40100 |  |  |  |  | mph | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0478_Wind_speed_mph
101 | Available | Holding Register | Wind speed max | 32-bit float | 480 |  | 40101 |  |  |  |  | mph | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0480_Wind_speed_max_mph
102 | Available | Holding Register | Barometric pressure hg | 32-bit float | 486 |  | 40102 |  |  |  |  | inHg | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0486_Barometric_pressure_hg_inHg
103 | Available | Holding Register | Barometric pressure sea level hg | 32-bit float | 488 |  | 40103 |  |  |  |  | inHg | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0488_Barometric_pressure_sea_level_hg_inHg
104 | Available | Holding Register | Rain instantaneous | 32-bit float | 502 |  | 40104 |  |  |  |  | in | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0502_Rain_instantaneous_in
105 | Available | Holding Register | Rain intensity | 32-bit float | 504 |  | 40105 |  |  |  |  | in/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0504_Rain_intensity_in_per_hr
106 | Available | Holding Register | Rain today | 32-bit float | 506 |  | 40106 |  |  |  |  | in/day | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0506_Rain_today_in_per_day
107 | Available | Holding Register | BOM temp 1 | 32-bit float | 522 |  | 40107 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0522_BOM_temp_1_DegF
108 | Available | Holding Register | BOM temp 2 | 32-bit float | 524 |  | 40108 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0524_BOM_temp_2_DegF
109 | Available | Holding Register | BOM temp 3 | 32-bit float | 526 |  | 40109 |  |  |  |  | DegF | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0526_BOM_temp_3_DegF
110 | Available | Holding Register | Modeled GHI | 32-bit float | 798 |  | 40110 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0798_Modeled_GHI_W_per_m2
111 | Available | Holding Register | Modeled DHI | 32-bit float | 800 |  | 40111 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0800_Modeled_DHI_W_per_m2
112 | Available | Holding Register | Modeled DNI | 32-bit float | 802 |  | 40112 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0802_Modeled_DNI_W_per_m2
113 | Available | Holding Register | Modeled POA | 32-bit float | 804 |  | 40113 |  |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0804_Modeled_POA_W_per_m2
114 | Available | Holding Register | Summary alarm | 32-bit unsigned int | 2000 |  | 40114 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2000_Summary_alarm
115 | Available | Holding Register | Data logger alarms register | 32-bit unsigned int | 2002 |  | 40115 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2002_Data_logger_alarms_register
116 | Available | Holding Register | Data logger watchdog error | Boolean | 2002 | 0 | 40116 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_watchdog_error
117 | Available | Holding Register | Data logger skipped main scan | Boolean | 2002 | 1 | 40117 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_skipped_main_scan
118 | Available | Holding Register | Data logger skipped slow scan | Boolean | 2002 | 2 | 40118 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_skipped_slow_scan
119 | Available | Holding Register | Data logger program variable out of bounds | Boolean | 2002 | 3 | 40119 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_program_variable_out_of_bounds
120 | Available | Holding Register | Data logger low 12V | Boolean | 2002 | 4 | 40120 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_12V
121 | Available | Holding Register | Data logger low 5V | Boolean | 2002 | 5 | 40121 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_5V
122 | Available | Holding Register | Data logger lithium battery error | Boolean | 2002 | 8 | 40122 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_lithium_battery_error
123 | Available | Holding Register | Data logger lithium battery low | Boolean | 2002 | 9 | 40123 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_lithium_battery_low
124 | Available | Holding Register | Data logger lithium battery critical | Boolean | 2002 | 10 | 40124 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_lithium_battery_critical
125 | Available | Holding Register | Data logger voltage error | Boolean | 2002 | 16 | 40125 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_voltage_error
126 | Available | Holding Register | Data logger low voltage warning | Boolean | 2002 | 17 | 40126 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_voltage_warning
127 | Available | Holding Register | Data logger low voltage | Boolean | 2002 | 18 | 40127 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_low_voltage
128 | Available | Holding Register | Data logger over voltage | Boolean | 2002 | 19 | 40128 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_over_voltage
129 | Available | Holding Register | Data logger temperature error | Boolean | 2002 | 24 | 40129 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_temperature_error
130 | Available | Holding Register | Data logger temperature below operating range | Boolean | 2002 | 25 | 40130 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_temperature_below_operating_range
131 | Available | Holding Register | Data logger temperature above operating range | Boolean | 2002 | 26 | 40131 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2002_Data_logger_temperature_above_operating_range
132 | Available | Holding Register | Battery alarms register | 32-bit unsigned int | 2004 |  | 40132 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2004_Battery_alarms_register
133 | Available | Holding Register | Check battery | Boolean | 2004 | 0 | 40133 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Check_battery
134 | Available | Holding Register | Battery voltage error | Boolean | 2004 | 8 | 40134 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Battery_voltage_error
135 | Available | Holding Register | Low battery voltage warning | Boolean | 2004 | 9 | 40135 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Low_battery_voltage_warning
136 | Available | Holding Register | Low battery voltage critical | Boolean | 2004 | 10 | 40136 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Low_battery_voltage_critical
137 | Available | Holding Register | Low battery voltage deep discharge | Boolean | 2004 | 11 | 40137 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Low_battery_voltage_deep_discharge
138 | Available | Holding Register | Battery current error | Boolean | 2004 | 16 | 40138 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Battery_current_error
139 | Available | Holding Register | Excessive battery current warning | Boolean | 2004 | 17 | 40139 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Excessive_battery_current_warning
140 | Available | Holding Register | Excessive battery current critical | Boolean | 2004 | 18 | 40140 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2004_Excessive_battery_current_critical
141 | Available | Holding Register | Charging alarms register | 32-bit unsigned int | 2006 |  | 40141 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Charging_alarms_register
142 | Available | Holding Register | Input voltage error | Boolean | 2006 | 0 | 40142 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Input_voltage_error
143 | Available | Holding Register | Rpu enabled | Boolean | 2006 | 1 | 40143 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Rpu_enabled
144 | Available | Holding Register | Input current error | Boolean | 2006 | 8 | 40144 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Input_current_error
145 | Available | Holding Register | Excessive input current | Boolean | 2006 | 9 | 40145 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Excessive_input_current
146 | Available | Holding Register | Load current error | Boolean | 2006 | 16 | 40146 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Load_current_error
147 | Available | Holding Register | Excessive load current warning | Boolean | 2006 | 17 | 40147 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Excessive_load_current_warning
148 | Available | Holding Register | Excessive load current | Boolean | 2006 | 18 | 40148 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2006_Excessive_load_current
149 | Available | Holding Register | GHI 1 alarms register | 32-bit unsigned int | 2018 |  | 40149 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2018_GHI_1_alarms_register
150 | Available | Holding Register | GHI 1 irradiance error | Boolean | 2018 | 0 | 40150 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_irradiance_error
151 | Available | Holding Register | GHI 1 irradiance negative | Boolean | 2018 | 1 | 40151 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_irradiance_negative
152 | Available | Holding Register | GHI 1 irradiance above solar constant | Boolean | 2018 | 2 | 40152 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_irradiance_above_solar_constant
153 | Available | Holding Register | GHI 1 temperature corrected irradiance error | Boolean | 2018 | 8 | 40153 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_temperature_corrected_irradiance_error
154 | Available | Holding Register | GHI 1 temperature corrected irradiance negative | Boolean | 2018 | 9 | 40154 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_temperature_corrected_irradiance_negative
155 | Available | Holding Register | GHI 1 temperature corrected irradiance above solar constant | Boolean | 2018 | 10 | 40155 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_temperature_corrected_irradiance_above_solar_constant
156 | Available | Holding Register | GHI 1 case temperature error | Boolean | 2018 | 16 | 40156 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_case_temperature_error
157 | Available | Holding Register | GHI 1 case temperature below operating range | Boolean | 2018 | 17 | 40157 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_case_temperature_below_operating_range
158 | Available | Holding Register | GHI 1 case temperature above operating range | Boolean | 2018 | 18 | 40158 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2018_GHI_1_case_temperature_above_operating_range
159 | Available | Holding Register | POA alarms register | 32-bit unsigned int | 2020 |  | 40159 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2020_POA_alarms_register
160 | Available | Holding Register | POA irradiance error | Boolean | 2020 | 0 | 40160 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_irradiance_error
161 | Available | Holding Register | POA irradiance negative | Boolean | 2020 | 1 | 40161 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_irradiance_negative
162 | Available | Holding Register | POA irradiance above solar constant | Boolean | 2020 | 2 | 40162 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_irradiance_above_solar_constant
163 | Available | Holding Register | POA temperature corrected irradiance error | Boolean | 2020 | 8 | 40163 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_temperature_corrected_irradiance_error
164 | Available | Holding Register | POA temperature corrected irradiance negative | Boolean | 2020 | 9 | 40164 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_temperature_corrected_irradiance_negative
165 | Available | Holding Register | POA temperature corrected irradiance above solar constant | Boolean | 2020 | 10 | 40165 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_temperature_corrected_irradiance_above_solar_constant
166 | Available | Holding Register | POA case temperature error | Boolean | 2020 | 16 | 40166 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_case_temperature_error
167 | Available | Holding Register | POA case temperature below operating range | Boolean | 2020 | 17 | 40167 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_case_temperature_below_operating_range
168 | Available | Holding Register | POA case temperature above operating range | Boolean | 2020 | 18 | 40168 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2020_POA_case_temperature_above_operating_range
169 | Available | Holding Register | GHI 2 alarms register | 32-bit unsigned int | 2022 |  | 40169 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2022_GHI_2_alarms_register
170 | Available | Holding Register | GHI 2 irradiance error | Boolean | 2022 | 0 | 40170 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_irradiance_error
171 | Available | Holding Register | GHI 2 irradiance negative | Boolean | 2022 | 1 | 40171 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_irradiance_negative
172 | Available | Holding Register | GHI 2 irradiance above solar constant | Boolean | 2022 | 2 | 40172 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_irradiance_above_solar_constant
173 | Available | Holding Register | GHI 2 temperature corrected irradiance error | Boolean | 2022 | 8 | 40173 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_temperature_corrected_irradiance_error
174 | Available | Holding Register | GHI 2 temperature corrected irradiance negative | Boolean | 2022 | 9 | 40174 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_temperature_corrected_irradiance_negative
175 | Available | Holding Register | GHI 2 temperature corrected irradiance above solar constant | Boolean | 2022 | 10 | 40175 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_temperature_corrected_irradiance_above_solar_constant
176 | Available | Holding Register | GHI 2 case temperature error | Boolean | 2022 | 16 | 40176 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_case_temperature_error
177 | Available | Holding Register | GHI 2 case temperature below operating range | Boolean | 2022 | 17 | 40177 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_case_temperature_below_operating_range
178 | Available | Holding Register | GHI 2 case temperature above operating range | Boolean | 2022 | 18 | 40178 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2022_GHI_2_case_temperature_above_operating_range
179 | Available | Holding Register | Multifunction alarms register | 32-bit unsigned int | 2038 |  | 40179 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2038_Multifunction_alarms_register
180 | Available | Holding Register | Ambient temperature error | Boolean | 2038 | 0 | 40180 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Ambient_temperature_error
181 | Available | Holding Register | Ambient temperature below operating range | Boolean | 2038 | 1 | 40181 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Ambient_temperature_below_operating_range
182 | Available | Holding Register | Ambient temperature above operating range | Boolean | 2038 | 2 | 40182 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Ambient_temperature_above_operating_range
183 | Available | Holding Register | Dew point error | Boolean | 2038 | 3 | 40183 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Dew_point_error
184 | Available | Holding Register | Dew point above ambient temperature | Boolean | 2038 | 4 | 40184 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Dew_point_above_ambient_temperature
185 | Available | Holding Register | Condensation warning | Boolean | 2038 | 5 | 40185 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Condensation_warning
186 | Available | Holding Register | Relative humidity error | Boolean | 2038 | 8 | 40186 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Relative_humidity_error
187 | Available | Holding Register | Relative humidity below operating range | Boolean | 2038 | 9 | 40187 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Relative_humidity_below_operating_range
188 | Available | Holding Register | Relative humidity above operating range | Boolean | 2038 | 10 | 40188 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Relative_humidity_above_operating_range
189 | Available | Holding Register | Absolute barometric pressure error | Boolean | 2038 | 16 | 40189 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Absolute_barometric_pressure_error
190 | Available | Holding Register | Absolute barometric pressure below operating range | Boolean | 2038 | 17 | 40190 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Absolute_barometric_pressure_below_operating_range
191 | Available | Holding Register | Absolute barometric pressure above operating range | Boolean | 2038 | 18 | 40191 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Absolute_barometric_pressure_above_operating_range
192 | Available | Holding Register | Sea level barometric pressure error | Boolean | 2038 | 24 | 40192 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Sea_level_barometric_pressure_error
193 | Available | Holding Register | Sea level barometric pressure below operating range | Boolean | 2038 | 25 | 40193 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Sea_level_barometric_pressure_below_operating_range
194 | Available | Holding Register | Sea level barometric pressure above operating range | Boolean | 2038 | 26 | 40194 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2038_Sea_level_barometric_pressure_above_operating_range
195 | Available | Holding Register | Wind alarms register | 32-bit unsigned int | 2040 |  | 40195 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2040_Wind_alarms_register
196 | Available | Holding Register | Wind speed error | Boolean | 2040 | 0 | 40196 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_error
197 | Available | Holding Register | Wind speed below operating range | Boolean | 2040 | 1 | 40197 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_below_operating_range
198 | Available | Holding Register | Wind speed above operating range | Boolean | 2040 | 2 | 40198 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_above_operating_range
199 | Available | Holding Register | Wind speed unable to execute measurement due to ambient conditions | Boolean | 2040 | 3 | 40199 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_unable_to_execute_measurement_due_to_ambient_conditions
200 | Available | Holding Register | Wind speed quality warning | Boolean | 2040 | 4 | 40200 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_quality_warning
201 | Available | Holding Register | Wind speed quality error | Boolean | 2040 | 5 | 40201 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_quality_error
202 | Available | Holding Register | Wind speed max error | Boolean | 2040 | 8 | 40202 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_max_error
203 | Available | Holding Register | Wind speed max below operating range | Boolean | 2040 | 9 | 40203 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_max_below_operating_range
204 | Available | Holding Register | Wind speed max above operating range | Boolean | 2040 | 10 | 40204 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_speed_max_above_operating_range
205 | Available | Holding Register | Wind direction error | Boolean | 2040 | 16 | 40205 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_direction_error
206 | Available | Holding Register | Wind direction below operating range | Boolean | 2040 | 17 | 40206 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_direction_below_operating_range
207 | Available | Holding Register | Wind direction above operating range | Boolean | 2040 | 18 | 40207 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Wind_direction_above_operating_range
208 | Available | Holding Register | Compass error | Boolean | 2040 | 24 | 40208 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Compass_error
209 | Available | Holding Register | Compass below operating range | Boolean | 2040 | 25 | 40209 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Compass_below_operating_range
210 | Available | Holding Register | Compass above operating range | Boolean | 2040 | 26 | 40210 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2040_Compass_above_operating_range
211 | Available | Holding Register | Rain alarms regsiter | 32-bit unsigned int | 2042 |  | 40211 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2042_Rain_alarms_regsiter
212 | Available | Holding Register | Rain total error | Boolean | 2042 | 0 | 40212 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_total_error
213 | Available | Holding Register | Rain total negative | Boolean | 2042 | 1 | 40213 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_total_negative
214 | Available | Holding Register | Rain total above operating range | Boolean | 2042 | 2 | 40214 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_total_above_operating_range
215 | Available | Holding Register | Rain intensity error | Boolean | 2042 | 8 | 40215 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_intensity_error
216 | Available | Holding Register | Rain intensity negative | Boolean | 2042 | 9 | 40216 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_intensity_negative
217 | Available | Holding Register | Rain intensity above operating range | Boolean | 2042 | 10 | 40217 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_intensity_above_operating_range
218 | Available | Holding Register | Rain today error | Boolean | 2042 | 16 | 40218 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_today_error
219 | Available | Holding Register | Rain today is negative | Boolean | 2042 | 17 | 40219 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_today_is_negative
220 | Available | Holding Register | Rain today above operating range | Boolean | 2042 | 18 | 40220 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2042_Rain_today_above_operating_range
221 | Available | Holding Register | BOM 1 alarm register | 32-bit unsigned int | 2058 |  | 40221 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2058_BOM_1_alarm_register
222 | Available | Holding Register | BOM 1 temperature error | Boolean | 2058 | 0 | 40222 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2058_BOM_1_temperature_error
223 | Available | Holding Register | BOM 1 temperature below operating range | Boolean | 2058 | 1 | 40223 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2058_BOM_1_temperature_below_operating_range
224 | Available | Holding Register | BOM 1 temperature above operating range | Boolean | 2058 | 2 | 40224 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2058_BOM_1_temperature_above_operating_range
225 | Available | Holding Register | BOM 2 alarm register | 32-bit unsigned int | 2060 |  | 40225 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2060_BOM_2_alarm_register
226 | Available | Holding Register | BOM 2 temperature error | Boolean | 2060 | 0 | 40226 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2060_BOM_2_temperature_error
227 | Available | Holding Register | BOM 2 temperature below operating range | Boolean | 2060 | 1 | 40227 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2060_BOM_2_temperature_below_operating_range
228 | Available | Holding Register | BOM 2 temperature above operating range | Boolean | 2060 | 2 | 40228 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2060_BOM_2_temperature_above_operating_range
229 | Available | Holding Register | BOM 3 alarm register | 32-bit unsigned int | 2062 |  | 40229 |  |  |  |  | unitless | 1 | [8 empty] | HREG_2062_BOM_3_alarm_register
230 | Available | Holding Register | BOM 3 temperature error | Boolean | 2062 | 0 | 40230 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2062_BOM_3_temperature_error
231 | Available | Holding Register | BOM 3 temperature below operating range | Boolean | 2062 | 1 | 40231 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2062_BOM_3_temperature_below_operating_range
232 | Available | Holding Register | BOM 3 temperature above operating range | Boolean | 2062 | 2 | 40232 |  | On (1) | Alarm | Normal | [10 empty] | HREG_2062_BOM_3_temperature_above_operating_range

## Soiling to PPC - Eclipse 1.0
Site Name | [5 empty] | Modbus |  |  |  | Soiling to PPC
Last updated |  | 2024-12-17 | Device Type | Groundwork Eclipse | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Environmental
Device Register Base |  | 1
Register Digits |  | 5
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Holding Register | Scan count | 32-bit float | 0 |  | 40001 |  |  |  | s | 1 | 1 | [7 empty] | HREG_0000_Scan_count_s
2 | Available | Holding Register | Skipped scans | 32-bit float | 2 |  | 40003 |  |  |  | count | 1 | 1 | [7 empty] | HREG_0002_Skipped_scans_count
3 | Available | Holding Register | Logger voltage | 32-bit float | 4 |  | 40005 |  |  |  | V | 1 | 1 | [7 empty] | HREG_0004_Logger_voltage_V
4 | Available | Holding Register | Logger temp | 32-bit float | 6 |  | 40007 |  |  |  | DegC | 1 | 1 | [7 empty] | HREG_0006_Logger_temp_DegC
5 | Available | Holding Register | Skipped slow scans | 32-bit float | 8 |  | 40009 |  |  |  | count | 1 | 1 | [7 empty] | HREG_0008_Skipped_slow_scans_count
6 | Available | Holding Register | Logger lithium | 32-bit float | 10 |  | 40011 |  |  |  | V | 1 | 1 | [7 empty] | HREG_0010_Logger_lithium_V
7 | Available | Holding Register | Logger low volt 12 | 32-bit float | 12 |  | 40013 |  |  |  | count | 1 | 1 | [7 empty] | HREG_0012_Logger_low_volt_12_count
8 | Available | Holding Register | Solar zenith | 32-bit float | 16 |  | 40017 |  |  |  | degrees | 1 | 1 | [7 empty] | HREG_0016_Solar_zenith_degrees
9 | Available | Holding Register | Solar elevation | 32-bit float | 18 |  | 40019 |  |  |  | degrees | 1 | 1 | [7 empty] | HREG_0018_Solar_elevation_degrees
10 | Available | Holding Register | Solar azimuth | 32-bit float | 20 |  | 40021 |  |  |  | degrees | 1 | 1 | [7 empty] | HREG_0020_Solar_azimuth_degrees
11 | Available | Holding Register | Logger data map version | 32-bit float | 24 |  | 40025 |  |  |  | unitless | 1 | 1 | [7 empty] | HREG_0024_Logger_data_map_version
12 | Available | Holding Register | Maint event | 32-bit float | 26 |  | 40027 |  |  |  | enumeration | 1 | 1 | [7 empty] | HREG_0026_Maint_event_enumaration | Soiling Status: 0 - Normal 1 - Maintenance in last 24 hours 2 - Normalization in last 5 minutes
13 | Available | Holding Register | ISC clean | 32-bit float | 138 |  | 40139 |  |  |  | A | 1 | 1 | [7 empty] | HREG_0138_ISC_clean_A
14 | Available | Holding Register | ISC soiled | 32-bit float | 140 |  | 40141 |  |  |  | A | 1 | 1 | [7 empty] | HREG_0140_ISC_soiled_A
15 | Available | Holding Register | Daily soiling loss factor | 32-bit float | 142 |  | 40143 |  |  |  | PU | 1 | 1 | [7 empty] | HREG_0142_Daily_soiling_loss_factor
16 | Available | Holding Register | Daily soiling ISC ratio | 32-bit float | 144 |  | 40145 |  |  |  | PU | 1 | 1 | [7 empty] | HREG_0144_Daily_soiling_ISC_ratio
17 | Available | Holding Register | BOM temp clean | 32-bit float | 146 |  | 40147 |  |  |  | DegC | 1 | 1 | [7 empty] | HREG_0146_BOM_temp_clean_DegC
18 | Available | Holding Register | BOM temp soiled | 32-bit float | 148 |  | 40149 |  |  |  | DegC | 1 | 1 | [7 empty] | HREG_0148_BOM_temp_soiled_DegC
19 | Available | Holding Register | Soiling loss factor | 32-bit float | 150 |  | 40151 |  |  |  | PU | 1 | 1 | [7 empty] | HREG_0150_Soiling_loss_factor
20 | Available | Holding Register | Soiling ISC ratio | 32-bit float | 152 |  | 40153 |  |  |  | PU | 1 | 1 | [7 empty] | HREG_0152_Soiling_ISC_ratio
21 | Available | Holding Register | ISC normalized soiled | 32-bit float | 154 |  | 40155 |  |  |  | A | 1 | 1 | [7 empty] | HREG_0154_ISC_normalized_soiled_A
22 | Available | Holding Register | G clean | 32-bit float | 156 |  | 40157 |  |  |  | W/m2 | 1 | 1 | [7 empty] | HREG_0156_G_clean_W_per_m2
23 | Available | Holding Register | G soiled | 32-bit float | 158 |  | 40159 |  |  |  | W/m2 | 1 | 1 | [7 empty] | HREG_0158_G_soiled_W_per_m2
24 | Available | Holding Register | Soiling status | 32-bit float | 160 |  | 40161 |  |  |  | enumeration | 1 | 1 | [7 empty] | HREG_0160_Soiling_status_enumeration | Soiling Status: 0 - Normal 1 - Maintenance in last 24 hours 2 - Normalization in last 5 minutes
25 | Available | Holding Register | Voc clean | 32-bit float | 162 |  | 40163 |  |  |  | V | 1 | 1 | [6 empty] | Voc clean | HREG_0162_Voc_clean_V
26 | Available | Holding Register | Voc soiled | 32-bit float | 164 |  | 40165 |  |  |  | V | 1 | 1 | [6 empty] | Voc soiled | HREG_0164_Voc_soiled_V
27 | Available | Holding Register | Hourly ISC clean avg | 32-bit float | 288 |  | 40289 |  |  |  | A | 1 | 1 | [7 empty] | HREG_0288_Hourly_ISC_clean_avg_A
28 | Available | Holding Register | Hourly ISC soiled avg | 32-bit float | 290 |  | 40291 |  |  |  | A | 1 | 1 | [7 empty] | HREG_0290_Hourly_ISC_soiled_avg_A
29 | Available | Holding Register | Hourly ISC normalized soiled | 32-bit float | 292 |  | 40293 |  |  |  | A | 1 | 1 | [7 empty] | HREG_0292_Hourly_ISC_normalized_soiled_A
30 | Available | Holding Register | Hourly BOM temp clean avg | 32-bit float | 296 |  | 40297 |  |  |  | DegC | 1 | 1 | [7 empty] | HREG_0296_Hourly_BOM_temp_clean_avg_DegC
31 | Available | Holding Register | Hourly BOM temp soiled avg | 32-bit float | 298 |  | 40299 |  |  |  | DegC | 1 | 1 | [7 empty] | HREG_0298_Hourly_BOM_temp_soiled_avg_DegC
32 | Available | Holding Register | Hourly soiling loss factor avg | 32-bit float | 300 |  | 40301 |  |  |  | PU | 1 | 1 | [7 empty] | HREG_0300_Hourly_soiling_loss_factor_avg
33 | Available | Holding Register | Hourly soiling ISC ratio avg | 32-bit float | 302 |  | 40303 |  |  |  | PU | 1 | 1 | [7 empty] | HREG_0302_Hourly_soiling_ISC_ratio_avg
34 | Available | Holding Register | Hourly G clean avg | 32-bit float | 304 |  | 40305 |  |  |  | W/m2 | 1 | 1 | [7 empty] | HREG_0304_Hourly_G_clean_avg_W_per_m2
35 | Available | Holding Register | Hourly G soiled avg | 32-bit float | 306 |  | 40307 |  |  |  | W/m2 | 1 | 1 | [7 empty] | HREG_0306_Hourly_G_soiled_avg_W_per_m2
36 | Available | Holding Register | Hourly VOC clean avg | 32-bit float | 308 |  | 40309 |  |  |  | V | 1 | [7 empty] | Hourly voc clean avg | HREG_0308_Hourly_VOC_clean_avg_V
37 | Available | Holding Register | Hourly VOC soiled avg | 32-bit float | 310 |  | 40311 |  |  |  | V | 1 | [7 empty] | Hourly voc soiled avg | HREG_0310_Hourly_VOC_soiled_avg_V
38 | Available | Holding Register | Logger temp | 32-bit float | 404 |  | 40405 |  |  |  | DegF | 1 | 1 | [7 empty] | HREG_0404_Logger_temp_degF
39 | Available | Holding Register | BOM temp clean | 32-bit float | 544 |  | 40545 |  |  |  | DegF | 1 | 1 | [7 empty] | HREG_0544_BOM_temp_clean_degF
40 | Available | Holding Register | BOM temp soiled | 32-bit float | 546 |  | 40547 |  |  |  | DegF | 1 | 1 | [7 empty] | HREG_0546_BOM_temp_soiled_degF
41 | Available | Holding Register | Daily soiling quality | 32-bit float | 616 |  | 40617 |  |  |  | % | 1 | 1 | [7 empty] | HREG_0616_Daily_soiling_quality_pct
42 | Available | Holding Register | Daily soiling age | 32-bit float | 618 |  | 40619 |  |  |  | days | 1 | 1 | [7 empty] | HREG_0618_Daily_soiling_age_days

## Soiling to PPC - DustIQ
Hornshadow | [5 empty] | Modbus |  |  |  | Soiling to PPC
Last updated |  | 2024-12-17 | Device Type | Groundwork Eclipse | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Environmental
Device Register Base |  | 1
Register Digits |  | 5
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Input Register | Soiling Ratio Sensor 1 | 16-bit Unsigned Integer | 20 |  | 30021 |  |  |  | % | 0.1 | 1 | [7 empty] | IREG_020_soiling_raio_1 |  | In steps of 0.1%, 9999 when not valid
2 | Available | Input Register | Transmission Loss Sensor 1 | 16-bit Signed Integer | 21 |  | 30022 |  |  |  | % | 0.1 | 1 | [7 empty] | IREG_021_transmission_loss_1 |  | In steps of 0.1%, 9999 when not valid
3 | Available | Input Register | Soiling Ratio Sensor 2 | 16-bit Unsigned Integer | 24 |  | 30025 |  |  |  | % | 0.1 | 1 | [7 empty] | IREG_024_soiling_ratio_2 |  | In steps of 0.1%, 9999 when not valid
4 | Available | Input Register | Transmission Loss Sensor 2 | 16-bit Signed Integer | 25 |  | 30026 |  |  |  | % | 0.1 | 1 | [7 empty] | IREG_025_transmission_loss_2 |  | In steps of 0.1%, 9999 when not valid
5 | Available | Input Register | Tilt X Direction ( Long Axis) | 16-bit Signed Integer | 28 |  | 30029 |  |  |  | Degrees | 0.1 | 1 | [7 empty] | IREG_028_tilt_x_deg |  | In steps of 0.1 degrees
6 | Available | Input Register | Tilt Y Direction (Short Axis) | 16-bit Signed Integer | 29 |  | 30030 |  |  |  | Degrees | 0.1 | 1 | [7 empty] | IREG_029_tilt_y_deg |  | In steps of 0.1 degrees
7 | Available | Input Register | Back Panel Temperature | 16-bit Unsigned Integer | 31 |  | 30032 |  |  |  | Deg K | 0.1 | 1 | [7 empty] | IREG_031_back_panel_temperature_K |  | In steps 0.1 Kelvin
8 | Available | Input Register | Device Voltage | 16-bit Unsigned Integer | 32 |  | 30033 |  |  |  | mV | 1 | 1 | [7 empty] | IREG_032_device_voltage_mV |  | Device voltage at the input connector
9 | Available | Input Register | Operational Mode | 16-bit Unsigned Integer | 33 |  | 30034 |  |  |  | degrees | 1 | 1 | [7 empty] | IREG_033_operational_mode | Normal = 1, Service = 2, Calibration = 3
10 | Available | Input Register | Device Status Flags | 16-bit Unsigned Integer | 34 |  | 30035 |  |  |  | degrees | 1 | 1 | [7 empty] | IREG_034_device_status | 0 = Status OK

## Albedometers to PPC
Site Name | [5 empty] | Modbus |  |  |  | Albedometers to PPC
Last updated |  | 2024-12-17 | Device Type | Groundwork Eclipse | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Environmental
Device Register Base |  | 1
Register Digits |  | 5
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Holding Register | Scan count | 32-bit float | 0 |  | 40001 |  |  |  | Sec | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0000_Scan_count_Sec
2 | Available | Holding Register | Skipped scans | 32-bit float | 2 |  | 40003 |  |  |  | Count | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0002_Skipped_scans_Count
3 | Available | Holding Register | Logger voltage | 32-bit float | 4 |  | 40005 |  |  |  | Volts DC | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0004_Logger_voltage_Volts DC
4 | Available | Holding Register | Logger temp | 32-bit float | 6 |  | 40007 |  |  |  | Deg C | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0006_Logger_temp_Deg C
5 | Available | Holding Register | Skipped slow scans | 32-bit float | 8 |  | 40009 |  |  |  | Count | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0008_Skipped_slow_scans_Count
6 | Available | Holding Register | Logger lithium | 32-bit float | 10 |  | 40011 |  |  |  | Volts DC | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0010_Logger_lithium_Volts DC
7 | Available | Holding Register | Logger low volt 12 | 32-bit float | 12 |  | 40013 |  |  |  | Count | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0012_Logger_low_volt_12_Count
8 | Available | Holding Register | Solar zenith | 32-bit float | 16 |  | 40017 |  |  |  | Degrees | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0016_Solar_zenith_Degrees |  | Calculated using lat, lon, elevation, Temp, pressure
9 | Available | Holding Register | Solar elevation | 32-bit float | 18 |  | 40019 |  |  |  | Degrees | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0018_Solar_elevation_Degrees |  | Calculated using lat, lon, elevation, Temp, pressure
10 | Available | Holding Register | Solar azimuth | 32-bit float | 20 |  | 40021 |  |  |  | Degrees | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0020_Solar_azimuth_Degrees |  | Calculated using lat, lon, elevation, Temp, pressure
11 | Available | Holding Register | Pyranometer heaters on/off | 32-bit float | 22 |  | 40023 |  |  |  | Enumeration | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0022_Pyranometer_heaters_on_off_Enumeration |  | 0 = Off, -1 = On. Heat_State on only when vent fan is running
12 | Available | Holding Register | Logger data map version | 32-bit float | 24 |  | 40025 |  |  |  | Unitless | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0024_Logger_data_map_version
13 | Available | Holding Register | Maint event | 32-bit float | 26 |  | 40027 |  | Maint ON | Maint OFF | Boolean | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0026_Maint_event_Boolean |  | 0 = nominal operation, 1 = maintenance button pushed in last five minutes
14 | Available | Holding Register | Logger AC Power | 32-bit float | 28 |  | 40029 |  | Normal | Alarm | Boolean | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0028_Logger_AC_Power_Boolean |  | 0 = no AC power, 1 = AC power
15 | Available | Holding Register | Battery Voltage | 32-bit float | 30 |  | 40031 |  |  |  | Volts DC | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0030_Battery_Voltage_Volts DC
16 | Available | Holding Register | Battery Current | 32-bit float | 32 |  | 40033 |  |  |  | Amps | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0032_Battery_Current_Amps |  | + if battery charging, - if battery discharging
17 | Available | Holding Register | Load Current | 32-bit float | 34 |  | 40035 |  |  |  | Amps | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0034_Load_Current_Amps
18 | Available | Holding Register | Solar Panel Voltage | 32-bit float | 36 |  | 40037 |  |  |  | Volts DC | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0036_Solar_Panel_Voltage_Volts DC |  | When both inputs are utilized, the higher voltage power source will be selected
19 | Available | Holding Register | Charge Source | 32-bit float | 40 |  | 40041 |  |  |  | Enumeration | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0040_Charge_Source_Enumeration |  | 0 = none, 1 = solar, 2 = AC/DC power supply
20 | Available | Holding Register | Battery Status | 32-bit float | 42 |  | 40043 |  | Alarm | Normal | Boolean | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0042_Battery_Status_Boolean |  | 0 = normal, 1 = check battery
21 | Available | Holding Register | Power Supply Voltage | 32-bit float | 44 |  | 40045 |  |  |  | Volts DC | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0044_Power_Supply_Voltage_Volts DC |  | When both inputs are utilized, the higher voltage power source will be selected
22 | Available | Holding Register | GHI | 32-bit float | 52 |  | 40053 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0052_GHI_W_per_m² |  | Warning: not Temp-corrected
23 | Available | Holding Register | GHI Temp Corr | 32-bit float | 54 |  | 40055 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0054_GHI_Temp_Corr_W_per_m² |  | Most accurate irradiance value
24 | Available | Holding Register | GHI Pyranometer Temp | 32-bit float | 56 |  | 40057 |  |  |  | Deg C | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0056_GHI_Pyranometer_Temp_Deg C
25 | Available | Holding Register | GHI Insolation | 32-bit float | 176 |  | 40177 |  |  |  | Wh/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0176_GHI_Insolation_Wh_per_m² |  | Previous 3-second scan total; divide by 1000 for kWh/m²
26 | Available | Holding Register | GHI Humidity | 32-bit float | 362 |  | 40363 |  |  |  | % | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0362_GHI_Humidity_pct |  | Used to detect desiccant failure
27 | Available | Holding Register | Reserved reserved | 32-bit float | 364 |  | 40365 |  |  |  | Reserved | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0364_Reserved_reserved_Reserved |  | Reserved
28 | Available | Holding Register | Pyranometer Single Axis Tilt | 32-bit float | 366 |  | 40367 |  |  |  | Degrees | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0366_Pyranometer_Single_Axis_Tilt_Degrees |  | Shows degrees from horizontal
29 | Available | Holding Register | Pyranometer Fan Speed | 32-bit float | 368 |  | 40369 |  |  |  | RPM | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0368_Pyranometer_Fan_Speed_RPM
30 | Available | Holding Register | Pyranometer Heater Current | 32-bit float | 370 |  | 40371 |  |  |  | mA | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0370_Pyranometer_Heater_Current_mA
31 | Available | Holding Register | Logger temp | 32-bit float | 404 |  | 40405 |  |  |  | Deg F | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0404_Logger_temp_Deg F
32 | Available | Holding Register | Albedometer GHI | 32-bit float | 596 |  | 40597 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0596_Albedometer_GHI_W_per_m² |  | Warning: not Temp-corrected.
33 | Available | Holding Register | Albedometer GHI Temp Corr | 32-bit float | 598 |  | 40599 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0598_Albedometer_GHI_Temp_Corr_W_per_m² |  | Most accurate irradiance value.
34 | Available | Holding Register | Ablendometer GHI Temp | 32-bit float | 600 |  | 40601 |  |  |  | Deg C | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0600_Ablendometer_GHI_Temp_Deg C
35 | Available | Holding Register | Albedometer RHI | 32-bit float | 602 |  | 40603 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0602_Albedometer_RHI_W_per_m² |  | Warning: not Temp-corrected.
36 | Available | Holding Register | Albedometer RHI Temp Corr | 32-bit float | 604 |  | 40605 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0604_Albedometer_RHI_Temp_Corr_W_per_m² |  | Most accurate irradiance value.
37 | Available | Holding Register | Abledometer RHI Temp | 32-bit float | 606 |  | 40607 |  |  |  | Deg C | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0606_Abledometer_RHI_Temp_Deg C
38 | Available | Holding Register | Albedo | 32-bit float | 608 |  | 40609 |  |  |  | PU | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0608_Albedo_PU |  | Calculated value: RHI_1 / GHI_1, See Daily_Albedo for filtered value
39 | Available | Holding Register | Albedo Temp Corr | 32-bit float | 610 |  | 40611 |  |  |  | PU | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0610_Albedo_Temp_Corr_PU |  | Calculated value: RHI_TC_1 / GHI_TC_1, See Daily_Albedo for filtered value
40 | Available | Holding Register | Daily Avg Albedo | 32-bit float | 612 |  | 40613 |  |  |  | PU | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0612_Daily_Avg_Albedo_PU |  | Avg of albedo values, solar noon ±30 minutes
41 | Available | Holding Register | Daily Avg Albedo Temp Corr | 32-bit float | 614 |  | 40615 |  |  |  | PU | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0614_Daily_Avg_Albedo_Temp_Corr_PU |  | Avg of Temp-corrected albedo values, solar noon ±30 minutes
42 | Available | Holding Register | Hourly Avg Abledometer GHI | 32-bit float | 646 |  | 40647 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0646_Hourly_Avg_Abledometer_GHI_W_per_m²
43 | Available | Holding Register | Hourly Avg Abledometer GHI Temp Corr | 32-bit float | 648 |  | 40649 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0648_Hourly_Avg_Abledometer_GHI_Temp_Corr_W_per_m²
44 | Available | Holding Register | Hourly Avg Albedometer GHI Temp | 32-bit float | 650 |  | 40651 |  |  |  | Deg C | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0650_Hourly_Avg_Albedometer_GHI_Temp_Deg C
45 | Available | Holding Register | Hourly Avg Albedometer RHI | 32-bit float | 652 |  | 40653 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0652_Hourly_Avg_Albedometer_RHI_W_per_m²
46 | Available | Holding Register | Hourly Avg Albedometer RHI Temp Corr | 32-bit float | 654 |  | 40655 |  |  |  | W/m² | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0654_Hourly_Avg_Albedometer_RHI_Temp_Corr_W_per_m²
47 | Available | Holding Register | Hourly Avg Albedometer RHI Temp | 32-bit float | 656 |  | 40657 |  |  |  | Deg C | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0656_Hourly_Avg_Albedometer_RHI_Temp_Deg C
48 | Available | Holding Register | Modeled GHI | 32-bit float | 798 |  | 40799 |  |  |  | W/m2 | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0798_Modeled_GHI_W_per_m2 |  | Ineichen Clear Sky Model**
49 | Available | Holding Register | Modeled DHI | 32-bit float | 800 |  | 40801 |  |  |  | W/m2 | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0800_Modeled_DHI_W_per_m2 |  | Ineichen Clear Sky Model**
50 | Available | Holding Register | Modeled DNI | 32-bit float | 802 |  | 40803 |  |  |  | W/m2 | 1 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 |  |  |  |  | HREG_0802_Modeled_DNI_W_per_m2 |  | Ineichen Clear Sky Model**

## Orbit POA to PPC
Site Name | [5 empty] | Modbus |  |  |  | Orbit POA to PPC
Last updated |  | 2024-04-01 | Device Type | Groundwork Orbit POA | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Environmental
Device Register Base |  | 1
Register Digits |  | 5
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Holding Register | Irradiance temperature compensated | 32-bit signed integer | 2 |  | 40003 |  |  |  |  | w/m2 | 100 | -2147483648 | 2147483647 | -21474836.48 | 21474836.47 |  |  |  |  | HREG_0002_Irradiance_temperature_compensated_w_per_m2
2 | Available | Holding Register | Irradiance | 32-bit signed integer | 4 |  | 40005 |  |  |  |  | w/m2 | 100 | -2147483648 | 2147483647 | -21474836.48 | 21474836.47 |  |  |  |  | HREG_0004_Irradiance_w_per_m2
3 | Available | Holding Register | Case temperature | 16-bit signed integer | 6 |  | 40007 |  |  |  |  | DegC | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  |  |  | HREG_0006_Case_temperature_DegC
4 | Available | Holding Register | Serial number | 16-bit unsigned integer | 40 |  | 40041 |  |  |  |  | unitless | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_0040_Serial_number
5 | Available | Holding Register | Calibration sensitivity | 32-bit float | 41 |  | 40042 |  |  |  |  | V / w/m2 | 1e-06 | -3.4028e+38 | 3.4028e+38 | -3.4028e+44 | 3.4028e+44 |  |  |  |  | HREG_0041_Calibration_sensitivity_V _per_ w_per_m2
6 | Available | Holding Register | Calibration date | 32-bit float | 46 |  | 40047 |  |  |  |  | BCD | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  |  |  | HREG_0046_Calibration_date_BCD |  | YYYYMMDD
7 | Available | Holding Register | Humidity | 16-bit unsigned integer | 98 |  | 40099 |  |  |  |  | % | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_0098_Humidity_pct
8 | Available | Holding Register | Tilt angle | 16-bit unsigned integer | 194 |  | 40195 |  |  |  |  | degrees | 100 | 0 | 65535 | 0 | 655.35 |  |  |  |  | HREG_0194_Tilt_angle_degrees
9 | Available | Holding Register | Fan speed | 16-bit unsigned integer | 196 |  | 40197 |  |  |  |  | RPM | 1 | 0 | 65535 | 0 | 65535 |  |  |  |  | HREG_0196_Fan_speed_RPM
10 | Available | Holding Register | Heater current | 16-bit unsigned integer | 199 |  | 40200 |  |  |  |  | A | 0.001 | 0 | 65535 | 0 | 65535000 |  |  |  |  | HREG_0199_Heater_current_A
Note on S6: Format: (Low-Low,Low,High,High-High)

## PPC to Ignition - SG3600
Earp | [5 empty] | DNP3.0 |  |  | PPC to Ignition - Inverters
Last updated |  | 2023-05-29 | Device Type | SG3600 |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Inverters
Replace [n] with PCU number written as 2 digits
List Index | Availability | Object | Point Description | Data Type | DNP index | Bit | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Analog input | Inv [n] status | 32-bit float | 0 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0000_Inv_[n]_status_enumeration | 0 to 4
2 | Available | Analog input | Inv [n] active power | 32-bit float | 1 |  | IREG_15099 | Analog |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,-10,3620,n/a | Out of Band | High resolution | KPI | AI_0001_Inv_[n]_active_power_kW
3 | Available | Analog input | Inv [n] reactive power | 32-bit float | 2 |  | IREG_15101 | Analog |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,-2180,2180,n/a | Out of Band | High resolution | KPI | AI_0002_Inv_[n]_reactive_power_kvar
4 | Available | Analog input | Inv [n] phase A current | 32-bit float | 3 |  | IREG_15096 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0003_Inv_[n]_phase_A_current_A
5 | Available | Analog input | Inv [n] phase B current | 32-bit float | 4 |  | IREG_15097 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0004_Inv_[n]_phase_B_current_A
6 | Available | Analog input | Inv [n] phase C current | 32-bit float | 5 |  | IREG_15098 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0005_Inv_[n]_phase_C_current_A
7 | Available | Analog input | Inv [n] phase AB voltage | 32-bit float | 6 |  | IREG_15093 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0006_Inv_[n]_phase_AB_voltage_V
8 | Available | Analog input | Inv [n] phase BC voltage | 32-bit float | 7 |  | IREG_15094 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0007_Inv_[n]_phase_BC_voltage_V
9 | Available | Analog input | Inv [n] phase CA voltage | 32-bit float | 8 |  | IREG_15095 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0008_Inv_[n]_phase_CA_voltage_V
10 | Available | Analog input | Inv [n] power factor | 32-bit float | 9 |  | IREG_15105 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0009_Inv_[n]_power_factor_PU
11 | Available | Analog input | Inv [n] frequency | 32-bit float | 10 |  | IREG_15106 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0010_Inv_[n]_frequency_Hz
12 | Available | Analog input | Inv [n] active power setpoint | 32-bit float | 11 |  | PPC Logic | Analog |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,0,3600,n/a | Out of Band | High resolution | KPI | AI_0011_Inv_[n]_active_power_setpoint_kW
13 | Available | Analog input | Inv [n] active power setpoint feedback | 32-bit float | 12 |  | IREG_15108 | Analog |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | AI_0010 +/- 1% | Not at Setpoint | High resolution | KPI | AI_0012_Inv_[n]_active_power_setpoint_feedback_kW
14 | Available | Analog input | Inv [n] reactive power mode | 32-bit signed integer | 13 |  | PPC Logic | State change |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Change events | KPI | AI_0013_Inv_[n]_reactive_power_mode_enumeration | 0 to 3, 98,99 | Q(U) and Q(P) modes are not used, but are defined
15 | Available | Analog input | Inv [n] reactive power mode feedback | 32-bit signed integer | 14 |  | PPC Logic | Analog |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 | AI_0012 +/- 1% | Not at Setpoint | Change events | KPI | AI_0014_Inv_[n]_reactive_power_mode_feedback_enumeration | 0 to 3, 98,99 | Q(U) and Q(P) modes are not used, but are defined
16 | Available | Analog input | Inv [n] reactive power setpoint | 32-bit float | 15 |  | PPC Logic | Analog |  |  | kvar or PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -2160,-1,1,2160 | 5-State | High resolution | KPI | AI_0015_Inv_[n]_reactive_power_setpoint_kvar or PU
17 | Available | Analog input | Inv [n] reactive power setpoint feedback | 32-bit float | 16 |  | IREG_15110 or IREG_15112 | Analog |  |  | kvar or PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | AI_0014 +/- 1% | Not at Setpoint | High resolution | KPI | AI_0016_Inv_[n]_reactive_power_setpoint_feedback_kvar or PU
18 | Available | Analog input | Inv [n] total DC power | 32-bit float | 17 |  | IREG_15091 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0017_Inv_[n]_total_DC_power_kW
19 | Available | Analog input | Inv [n] energy production today | 32-bit float | 18 |  | IREG_15072 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0018_Inv_[n]_energy_production_today_kWh
20 | Available | Analog input | Inv [n] energy production yesterday | 32-bit float | 19 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0019_Inv_[n]_energy_production_yesterday_kWh
21 | Available | Analog input | Inv [n] total energy production | 32-bit float | 20 |  | IREG_15076 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0020_Inv_[n]_total_energy_production_kWh
22 | Available | Analog input | Inv [n] total running hours | 32-bit float | 21 |  | IREG_15081 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0021_Inv_[n]_total_running_hours_hr
23 | Available | Analog input | Inv [n] transformer oil temperature | 32-bit float | 22 |  | IREG_15118 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -40,-25,50,60 | 5-State | Low resolution | Secondary Detail | AI_0022_Inv_[n]_transformer_oil_temperature_degC
24 | Available | Analog input | Inv [n] transformer winding temperature | 32-bit float | 23 |  | IREG_15119 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -40,-25,50,60 | 5-State | Low resolution | Secondary Detail | AI_0023_Inv_[n]_transformer_winding_temperature_degC
25 | Available | Analog input | Inv [n] maximum appearant power | 32-bit float | 24 |  | IREG_15704 | Analog |  |  | kVA | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,3600,3600,n/a | Out of Band | Low resolution | Diagnostic | AI_0024_Inv_[n]_maximum_appearant_power_kVA |  | Real time derating
26 | Available | Analog input | Inv [n] maximum lagging reactive power | 32-bit float | 25 |  | IREG_15706 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0025_Inv_[n]_maximum_lagging_reactive_power_kvar
27 | Available | Analog input | Inv [n] maximum leading reactive power | 32-bit float | 26 |  | IREG_15707 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0026_Inv_[n]_maximum_leading_reactive_power_kvar
28 | Available | Analog input | Inv [n] zone monitor status | 32-bit signed integer | 27 |  | IREG_15999 | None |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Change events | Diagnostic | AI_0027_Inv_[n]_zone_monitor_status_enumeration | 0 to 2
29 | Available | Analog input | Inv [n] spare analog 01 | 32-bit float | 28 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0028_Inv_[n]_spare_analog_01
30 | Available | Analog input | Inv [n] spare analog 02 | 32-bit float | 29 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0029_Inv_[n]_spare_analog_02
31 | Available | Analog input | Inv [n] spare analog 03 | 32-bit float | 30 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0030_Inv_[n]_spare_analog_03
32 | Available | Analog input | Inv [n] spare analog 04 | 32-bit float | 31 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0031_Inv_[n]_spare_analog_04
33 | Available | Analog input | Inv [n] spare analog 05 | 32-bit float | 32 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0032_Inv_[n]_spare_analog_05
34 | Available | Analog input | Inv [n] spare analog 06 | 32-bit float | 33 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0033_Inv_[n]_spare_analog_06
35 | Available | Analog input | Inv [n] spare analog 07 | 32-bit float | 34 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0034_Inv_[n]_spare_analog_07
36 | Available | Analog input | Inv [n] spare analog 08 | 32-bit float | 35 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0035_Inv_[n]_spare_analog_08
37 | Available | Analog input | Inv [n] spare analog 09 | 32-bit float | 36 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0036_Inv_[n]_spare_analog_09
38 | Available | Analog input | Inv [n] spare analog 10 | 32-bit float | 37 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0037_Inv_[n]_spare_analog_10
39 | Available | Analog input | Inv [n] unit 1 status | 32-bit float | 38 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0038_Inv_[n]_unit_1_status_enumeration | 0 to 4
40 | Available | Analog input | Inv [n] unit 1 active power | 32-bit float | 39 |  | IREG_15169 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0039_Inv_[n]_unit_1_active_power_kW
41 | Available | Analog input | Inv [n] unit 1 reactive power | 32-bit float | 40 |  | IREG_15171 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0040_Inv_[n]_unit_1_reactive_power_kvar
42 | Available | Analog input | Inv [n] unit 1 phase A current | 32-bit float | 41 |  | IREG_15166 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0041_Inv_[n]_unit_1_phase_A_current_A
43 | Available | Analog input | Inv [n] unit 1 phase B current | 32-bit float | 42 |  | IREG_15167 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0042_Inv_[n]_unit_1_phase_B_current_A |  | True if any alarm is set for this inverter
44 | Available | Analog input | Inv [n] unit 1 phase C current | 32-bit float | 43 |  | IREG_15168 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0043_Inv_[n]_unit_1_phase_C_current_A
45 | Available | Analog input | Inv [n] unit 1 phase AB voltage | 32-bit float | 44 |  | IREG_15163 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0044_Inv_[n]_unit_1_phase_AB_voltage_V
46 | Available | Analog input | Inv [n] unit 1 phase BC voltage | 32-bit float | 45 |  | IREG_15164 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0045_Inv_[n]_unit_1_phase_BC_voltage_V
47 | Available | Analog input | Inv [n] unit 1 phase CA voltage | 32-bit float | 46 |  | IREG_15165 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0046_Inv_[n]_unit_1_phase_CA_voltage_V
48 | Available | Analog input | Inv [n] unit 1 power factor | 32-bit float | 47 |  | IREG_15173 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0047_Inv_[n]_unit_1_power_factor_PU
49 | Available | Analog input | Inv [n] unit 1 frequency | 32-bit float | 48 |  | IREG_15174 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0048_Inv_[n]_unit_1_frequency_Hz
50 | Available | Analog input | Inv [n] unit 1 DC power | 32-bit float | 49 |  | IREG_15161 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0049_Inv_[n]_unit_1_DC_power_kW
51 | Available | Analog input | Inv [n] unit 1 total DC current | 32-bit float | 50 |  | IREG_15160 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0050_Inv_[n]_unit_1_total_DC_current_A
52 | Available | Analog input | Inv [n] unit 1 DC voltage | 32-bit float | 51 |  | IREG_15159 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0051_Inv_[n]_unit_1_DC_voltage_V
53 | Available | Analog input | Inv [n] unit 1 energy production today | 32-bit float | 52 |  | IREG_15149 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0052_Inv_[n]_unit_1_energy_production_today_kWh
54 | Available | Analog input | Inv [n] unit 1 energy production yesterday | 32-bit float | 53 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0053_Inv_[n]_unit_1_energy_production_yesterday_kWh
55 | Available | Analog input | Inv [n] unit 1 total energy production | 32-bit float | 54 |  | IREG_15153 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0054_Inv_[n]_unit_1_total_energy_production_kWh
56 | Available | Analog input | Inv [n] unit 1 total running hours | 32-bit float | 55 |  | IREG_15156 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0055_Inv_[n]_unit_1_total_running_hours_hr
57 | Available | Analog input | Inv [n] unit 1 internal module temperature | 32-bit float | 56 |  | IREG_15158 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -40,-25,50,60 | 5-State | Low resolution | Diagnostic | AI_0056_Inv_[n]_unit_1_internal_module_temperature_degC
58 | Available | Analog input | Inv [n] unit 1 yesterday grid connected minutes | 32-bit float | 57 |  | PPC Logic | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0057_Inv_[n]_unit_1_yesterday_grid_connected_minutes_min
59 | Available | Analog input | Inv [n] unit 1 efficiency | 32-bit float | 58 |  | IREG_15175 | None |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0058_Inv_[n]_unit_1_efficiency_pct
60 | Available | Analog input | Inv [n] unit 1 positive resitance to ground | 32-bit float | 59 |  | IREG_15203 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0059_Inv_[n]_unit_1_positive_resitance_to_ground_kOhm
61 | Available | Analog input | Inv [n] unit 1 negative resitance to ground | 32-bit float | 60 |  | IREG_15205 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0060_Inv_[n]_unit_1_negative_resitance_to_ground_kOhm
62 | Available | Analog input | Inv [n] unit 1 negative voltage to ground | 32-bit float | 61 |  | IREG_15211 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0061_Inv_[n]_unit_1_negative_voltage_to_ground_V
63 | Available | Analog input | Inv [n] unit 1 DC Input 1 | 32-bit float | 62 |  | IREG_15029 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0062_Inv_[n]_unit_1_DC_Input_1_A
64 | Available | Analog input | Inv [n] unit 1 DC Input 2 | 32-bit float | 63 |  | IREG_15030 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0063_Inv_[n]_unit_1_DC_Input_2_A
65 | Available | Analog input | Inv [n] unit 1 DC Input 3 | 32-bit float | 64 |  | IREG_15031 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0064_Inv_[n]_unit_1_DC_Input_3_A
66 | Available | Analog input | Inv [n] unit 1 DC Input 4 | 32-bit float | 65 |  | IREG_15032 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0065_Inv_[n]_unit_1_DC_Input_4_A
67 | Available | Analog input | Inv [n] unit 1 DC Input 5 | 32-bit float | 66 |  | IREG_15033 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0066_Inv_[n]_unit_1_DC_Input_5_A
68 | Available | Analog input | Inv [n] unit 1 DC Input 6 | 32-bit float | 67 |  | IREG_15034 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0067_Inv_[n]_unit_1_DC_Input_6_A
69 | Available | Analog input | Inv [n] unit 1 DC Input 7 | 32-bit float | 68 |  | IREG_15035 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0068_Inv_[n]_unit_1_DC_Input_7_A
70 | Available | Analog input | Inv [n] unit 1 DC Input 8 | 32-bit float | 69 |  | IREG_15036 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0069_Inv_[n]_unit_1_DC_Input_8_A
71 | Available | Analog input | Inv [n] unit 1 DC Input 9 | 32-bit float | 70 |  | IREG_15037 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0070_Inv_[n]_unit_1_DC_Input_9_A
72 | Available | Analog input | Inv [n] unit 1 DC Input 10 | 32-bit float | 71 |  | IREG_15038 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0071_Inv_[n]_unit_1_DC_Input_10_A
73 | Available | Analog input | Inv [n] unit 1 DC Input 11 | 32-bit float | 72 |  | IREG_15039 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0072_Inv_[n]_unit_1_DC_Input_11_A
74 | Available | Analog input | Inv [n] unit 1 DC Input 12 | 32-bit float | 73 |  | IREG_15040 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0073_Inv_[n]_unit_1_DC_Input_12_A
75 | Available | Analog input | Inv [n] unit 1 DC Input 13 | 32-bit float | 74 |  | IREG_15041 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0074_Inv_[n]_unit_1_DC_Input_13_A
76 | Available | Analog input | Inv [n] unit 1 DC Input 14 | 32-bit float | 75 |  | IREG_15042 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0075_Inv_[n]_unit_1_DC_Input_14_A
77 | Available | Analog input | Inv [n] unit 1 DC Input 15 | 32-bit float | 76 |  | IREG_15043 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0076_Inv_[n]_unit_1_DC_Input_15_A
78 | Available | Analog input | Inv [n] unit 1 DC Input 16 | 32-bit float | 77 |  | IREG_15044 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0077_Inv_[n]_unit_1_DC_Input_16_A
79 | Available | Analog input | Inv [n] unit 1 event recorder record count | 32-bit float | 78 |  | IREG_15733 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0078_Inv_[n]_unit_1_event_recorder_record_count_count
80 | Available | Analog input | Inv [n] unit 1 AC cabinet temperature | 32-bit float | 79 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0079_Inv_[n]_unit_1_AC_cabinet_temperature_degC
81 | Available | Analog input | Inv [n] unit 1 DC cabinet temperature | 32-bit float | 80 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0080_Inv_[n]_unit_1_DC_cabinet_temperature_degC
82 | Available | Analog input | Inv [n] unit 1 control cabinet temperature | 32-bit float | 81 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0081_Inv_[n]_unit_1_control_cabinet_temperature_degC
83 | Available | Analog input | Inv [n] unit 1 busbar temperature | 32-bit float | 82 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0082_Inv_[n]_unit_1_busbar_temperature_degC
84 | Available | Analog input | Inv [n] unit 1 module cabinet temperature | 32-bit float | 83 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0083_Inv_[n]_unit_1_module_cabinet_temperature_degC
85 | Available | Analog input | Inv [n] unit 1 reactor cabinet temperature | 32-bit float | 84 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0084_Inv_[n]_unit_1_reactor_cabinet_temperature_degC
86 | Available | Analog input | Inv [n] unit 1 spare analog 01 | 32-bit float | 85 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0085_Inv_[n]_unit_1_spare_analog_01
87 | Available | Analog input | Inv [n] unit 1 spare analog 02 | 32-bit float | 86 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0086_Inv_[n]_unit_1_spare_analog_02
88 | Available | Analog input | Inv [n] unit 1 spare analog 03 | 32-bit float | 87 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0087_Inv_[n]_unit_1_spare_analog_03
89 | Available | Analog input | Inv [n] unit 1 spare analog 04 | 32-bit float | 88 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0088_Inv_[n]_unit_1_spare_analog_04
90 | Available | Analog input | Inv [n] unit 1 spare analog 05 | 32-bit float | 89 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0089_Inv_[n]_unit_1_spare_analog_05
91 | Available | Analog input | Inv [n] unit 1 spare analog 06 | 32-bit float | 90 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0090_Inv_[n]_unit_1_spare_analog_06
92 | Available | Analog input | Inv [n] unit 1 spare analog 07 | 32-bit float | 91 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0091_Inv_[n]_unit_1_spare_analog_07
93 | Available | Analog input | Inv [n] unit 1 spare analog 08 | 32-bit float | 92 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0092_Inv_[n]_unit_1_spare_analog_08
94 | Available | Analog input | Inv [n] unit 1 spare analog 09 | 32-bit float | 93 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0093_Inv_[n]_unit_1_spare_analog_09
95 | Available | Analog input | Inv [n] unit 1 spare analog 10 | 32-bit float | 94 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0094_Inv_[n]_unit_1_spare_analog_10
96 | Available | Analog input | Inv [n] unit 2 status | 32-bit float | 95 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0095_Inv_[n]_unit_2_status_enumeration | 0 to 4
97 | Available | Analog input | Inv [n] unit 2 active power | 32-bit float | 96 |  | IREG_15169 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0096_Inv_[n]_unit_2_active_power_kW
98 | Available | Analog input | Inv [n] unit 2 reactive power | 32-bit float | 97 |  | IREG_15171 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0097_Inv_[n]_unit_2_reactive_power_kvar
99 | Available | Analog input | Inv [n] unit 2 phase A current | 32-bit float | 98 |  | IREG_15166 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0098_Inv_[n]_unit_2_phase_A_current_A
100 | Available | Analog input | Inv [n] unit 2 phase B current | 32-bit float | 99 |  | IREG_15167 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0099_Inv_[n]_unit_2_phase_B_current_A
101 | Available | Analog input | Inv [n] unit 2 phase C current | 32-bit float | 100 |  | IREG_15168 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0100_Inv_[n]_unit_2_phase_C_current_A
102 | Available | Analog input | Inv [n] unit 2 phase AB voltage | 32-bit float | 101 |  | IREG_15163 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0101_Inv_[n]_unit_2_phase_AB_voltage_V
103 | Available | Analog input | Inv [n] unit 2 phase BC voltage | 32-bit float | 102 |  | IREG_15164 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0102_Inv_[n]_unit_2_phase_BC_voltage_V
104 | Available | Analog input | Inv [n] unit 2 phase CA voltage | 32-bit float | 103 |  | IREG_15165 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0103_Inv_[n]_unit_2_phase_CA_voltage_V
105 | Available | Analog input | Inv [n] unit 2 power factor | 32-bit float | 104 |  | IREG_15173 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0104_Inv_[n]_unit_2_power_factor_PU
106 | Available | Analog input | Inv [n] unit 2 frequency | 32-bit float | 105 |  | IREG_15174 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0105_Inv_[n]_unit_2_frequency_Hz
107 | Available | Analog input | Inv [n] unit 2 DC power | 32-bit float | 106 |  | IREG_15161 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0106_Inv_[n]_unit_2_DC_power_kW
108 | Available | Analog input | Inv [n] unit 2 total DC current | 32-bit float | 107 |  | IREG_15160 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0107_Inv_[n]_unit_2_total_DC_current_A
109 | Available | Analog input | Inv [n] unit 2 DC voltage | 32-bit float | 108 |  | IREG_15159 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0108_Inv_[n]_unit_2_DC_voltage_V
110 | Available | Analog input | Inv [n] unit 2 energy production today | 32-bit float | 109 |  | IREG_15149 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0109_Inv_[n]_unit_2_energy_production_today_kWh
111 | Available | Analog input | Inv [n] unit 2 energy production yesterday | 32-bit float | 110 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0110_Inv_[n]_unit_2_energy_production_yesterday_kWh
112 | Available | Analog input | Inv [n] unit 2 total energy production | 32-bit float | 111 |  | IREG_15153 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0111_Inv_[n]_unit_2_total_energy_production_kWh
113 | Available | Analog input | Inv [n] unit 2 total running hours | 32-bit float | 112 |  | IREG_15156 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0112_Inv_[n]_unit_2_total_running_hours_hr
114 | Available | Analog input | Inv [n] unit 2 internal module temperature | 32-bit float | 113 |  | IREG_15158 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -40,-25,50,60 | 5-State | Low resolution | Diagnostic | AI_0113_Inv_[n]_unit_2_internal_module_temperature_degC
115 | Available | Analog input | Inv [n] unit 2 yesterday grid connected minutes | 32-bit float | 114 |  | PPC Logic | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0114_Inv_[n]_unit_2_yesterday_grid_connected_minutes_min
116 | Available | Analog input | Inv [n] unit 2 efficiency | 32-bit float | 115 |  | IREG_15175 | None |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0115_Inv_[n]_unit_2_efficiency_pct
117 | Available | Analog input | Inv [n] unit 2 positive resitance to ground | 32-bit float | 116 |  | IREG_15203 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0116_Inv_[n]_unit_2_positive_resitance_to_ground_kOhm
118 | Available | Analog input | Inv [n] unit 2 negative resitance to ground | 32-bit float | 117 |  | IREG_15205 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0117_Inv_[n]_unit_2_negative_resitance_to_ground_kOhm
119 | Available | Analog input | Inv [n] unit 2 negative voltage to ground | 32-bit float | 118 |  | IREG_15211 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0118_Inv_[n]_unit_2_negative_voltage_to_ground_V
120 | Available | Analog input | Inv [n] unit 2 DC Input 1 | 32-bit float | 119 |  | IREG_15029 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0119_Inv_[n]_unit_2_DC_Input_1_A
121 | Available | Analog input | Inv [n] unit 2 DC Input 2 | 32-bit float | 120 |  | IREG_15030 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0120_Inv_[n]_unit_2_DC_Input_2_A
122 | Available | Analog input | Inv [n] unit 2 DC Input 3 | 32-bit float | 121 |  | IREG_15031 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0121_Inv_[n]_unit_2_DC_Input_3_A
123 | Available | Analog input | Inv [n] unit 2 DC Input 4 | 32-bit float | 122 |  | IREG_15032 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0122_Inv_[n]_unit_2_DC_Input_4_A
124 | Available | Analog input | Inv [n] unit 2 DC Input 5 | 32-bit float | 123 |  | IREG_15033 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0123_Inv_[n]_unit_2_DC_Input_5_A
125 | Available | Analog input | Inv [n] unit 2 DC Input 6 | 32-bit float | 124 |  | IREG_15034 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0124_Inv_[n]_unit_2_DC_Input_6_A
126 | Available | Analog input | Inv [n] unit 2 DC Input 7 | 32-bit float | 125 |  | IREG_15035 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0125_Inv_[n]_unit_2_DC_Input_7_A
127 | Available | Analog input | Inv [n] unit 2 DC Input 8 | 32-bit float | 126 |  | IREG_15036 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0126_Inv_[n]_unit_2_DC_Input_8_A
128 | Available | Analog input | Inv [n] unit 2 DC Input 9 | 32-bit float | 127 |  | IREG_15037 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0127_Inv_[n]_unit_2_DC_Input_9_A
129 | Available | Analog input | Inv [n] unit 2 DC Input 10 | 32-bit float | 128 |  | IREG_15038 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0128_Inv_[n]_unit_2_DC_Input_10_A
130 | Available | Analog input | Inv [n] unit 2 DC Input 11 | 32-bit float | 129 |  | IREG_15039 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0129_Inv_[n]_unit_2_DC_Input_11_A
131 | Available | Analog input | Inv [n] unit 2 DC Input 12 | 32-bit float | 130 |  | IREG_15040 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0130_Inv_[n]_unit_2_DC_Input_12_A
132 | Available | Analog input | Inv [n] unit 2 DC Input 13 | 32-bit float | 131 |  | IREG_15041 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0131_Inv_[n]_unit_2_DC_Input_13_A
133 | Available | Analog input | Inv [n] unit 2 DC Input 14 | 32-bit float | 132 |  | IREG_15042 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0132_Inv_[n]_unit_2_DC_Input_14_A
134 | Available | Analog input | Inv [n] unit 2 DC Input 15 | 32-bit float | 133 |  | IREG_15043 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0133_Inv_[n]_unit_2_DC_Input_15_A
135 | Available | Analog input | Inv [n] unit 2 DC Input 16 | 32-bit float | 134 |  | IREG_15044 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0134_Inv_[n]_unit_2_DC_Input_16_A
136 | Available | Analog input | Inv [n] unit 2 event recorder record count | 32-bit float | 135 |  | IREG_15734 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0135_Inv_[n]_unit_2_event_recorder_record_count_count
137 | Available | Analog input | Inv [n] unit 2 AC cabinet temperature | 32-bit float | 136 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0136_Inv_[n]_unit_2_AC_cabinet_temperature_degC
138 | Available | Analog input | Inv [n] unit 2 DC cabinet temperature | 32-bit float | 137 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0137_Inv_[n]_unit_2_DC_cabinet_temperature_degC
139 | Available | Analog input | Inv [n] unit 2 control cabinet temperature | 32-bit float | 138 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0138_Inv_[n]_unit_2_control_cabinet_temperature_degC
140 | Available | Analog input | Inv [n] unit 2 busbar temperature | 32-bit float | 139 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0139_Inv_[n]_unit_2_busbar_temperature_degC
141 | Available | Analog input | Inv [n] unit 2 module cabinet temperature | 32-bit float | 140 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0140_Inv_[n]_unit_2_module_cabinet_temperature_degC
142 | Available | Analog input | Inv [n] unit 2 reactor cabinet temperature | 32-bit float | 141 |  | TBD | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0141_Inv_[n]_unit_2_reactor_cabinet_temperature_degC
143 | Available | Analog input | Inv [n] unit 2 spare analog 01 | 32-bit float | 142 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0142_Inv_[n]_unit_2_spare_analog_01
144 | Available | Analog input | Inv [n] unit 2 spare analog 02 | 32-bit float | 143 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0143_Inv_[n]_unit_2_spare_analog_02
145 | Available | Analog input | Inv [n] unit 2 spare analog 03 | 32-bit float | 144 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0144_Inv_[n]_unit_2_spare_analog_03
146 | Available | Analog input | Inv [n] unit 2 spare analog 04 | 32-bit float | 145 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0145_Inv_[n]_unit_2_spare_analog_04
147 | Available | Analog input | Inv [n] unit 2 spare analog 05 | 32-bit float | 146 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0146_Inv_[n]_unit_2_spare_analog_05
148 | Available | Analog input | Inv [n] unit 2 spare analog 06 | 32-bit float | 147 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0147_Inv_[n]_unit_2_spare_analog_06
149 | Available | Analog input | Inv [n] unit 2 spare analog 07 | 32-bit float | 148 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0148_Inv_[n]_unit_2_spare_analog_07
150 | Available | Analog input | Inv [n] unit 2 spare analog 08 | 32-bit float | 149 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0149_Inv_[n]_unit_2_spare_analog_08
151 | Available | Analog input | Inv [n] unit 2 spare analog 09 | 32-bit float | 150 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0150_Inv_[n]_unit_2_spare_analog_09
152 | Available | Analog input | Inv [n] unit 2 spare analog 10 | 32-bit float | 151 | [6 empty] | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0151_Inv_[n]_unit_2_spare_analog_10
153 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 1 | 32-bit signed integer | 152 |  | IREG_16004 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0152_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_1_count
154 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 2 | 32-bit signed integer | 153 |  | IREG_16005 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0153_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_2_count
155 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 3 | 32-bit signed integer | 154 |  | IREG_16006 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0154_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_3_count
156 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 4 | 32-bit signed integer | 155 |  | IREG_16007 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0155_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_4_count
157 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 5 | 32-bit signed integer | 156 |  | IREG_16008 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0156_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_5_count
158 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 6 | 32-bit signed integer | 157 |  | IREG_16009 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0157_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_6_count
159 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 7 | 32-bit signed integer | 158 |  | IREG_16010 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0158_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_7_count
160 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 8 | 32-bit signed integer | 159 |  | IREG_16011 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0159_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_8_count
161 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 9 | 32-bit signed integer | 160 |  | IREG_16012 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0160_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_9_count
162 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 10 | 32-bit signed integer | 161 |  | IREG_16013 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0161_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_10_count
163 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 11 | 32-bit signed integer | 162 |  | IREG_16014 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0162_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_11_count
164 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 12 | 32-bit signed integer | 163 |  | IREG_16015 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0163_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_12_count
165 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 13 | 32-bit signed integer | 164 |  | IREG_16016 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0164_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_13_count
166 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 14 | 32-bit signed integer | 165 |  | IREG_16017 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0165_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_14_count
167 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 15 | 32-bit signed integer | 166 |  | IREG_16018 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0166_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_15_count
168 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 16 | 32-bit signed integer | 167 |  | IREG_16019 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0167_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_16_count
169 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 1 | 32-bit signed integer | 168 |  | IREG_16020 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0168_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_1_count
170 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 2 | 32-bit signed integer | 169 |  | IREG_16021 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0169_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_2_count
171 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 3 | 32-bit signed integer | 170 |  | IREG_16022 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0170_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_3_count
172 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 4 | 32-bit signed integer | 171 |  | IREG_16023 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0171_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_4_count
173 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 5 | 32-bit signed integer | 172 |  | IREG_16024 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0172_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_5_count
174 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 6 | 32-bit signed integer | 173 |  | IREG_16025 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0173_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_6_count
175 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 7 | 32-bit signed integer | 174 |  | IREG_16026 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0174_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_7_count
176 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 8 | 32-bit signed integer | 175 |  | IREG_16027 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0175_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_8_count
177 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 9 | 32-bit signed integer | 176 |  | IREG_16028 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0176_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_9_count
178 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 10 | 32-bit signed integer | 177 |  | IREG_16029 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0177_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_10_count
179 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 11 | 32-bit signed integer | 178 |  | IREG_16030 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0178_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_11_count
180 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 12 | 32-bit signed integer | 179 |  | IREG_16031 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0179_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_12_count
181 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 13 | 32-bit signed integer | 180 |  | IREG_16032 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0180_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_13_count
182 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 14 | 32-bit signed integer | 181 |  | IREG_16033 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0181_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_14_count
183 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 15 | 32-bit signed integer | 182 |  | IREG_16034 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0182_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_15_count
184 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 16 | 32-bit signed integer | 183 |  | IREG_16035 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0183_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_16_count
185 | Available | Counter | Inv [n] status | 32-bit bitfield | 0 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0000_Inv_[n]_status
186 | Available | Counter | Inv [n] circuit breaker status | 32-bit bitfield | 0 | 0 | IREG_15113.10 | None | Open | Closed | [8 empty] | Change events | Primary Detail | CNT_0000_Inv_[n]_circuit_breaker_status
187 | Available | Counter | Inv [n] disconnector status | 32-bit bitfield | 0 | 1 | IREG_15113.11 | None | Open | Closed | [8 empty] | Change events | Primary Detail | CNT_0000_Inv_[n]_disconnector_status
188 | Available | Counter | Inv [n] MV load switch status | 32-bit bitfield | 0 | 2 | IREG_15130.0 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0000_Inv_[n]_MV_load_switch_status
189 | Available | Counter | Inv [n] HV local remote switch status | 32-bit bitfield | 0 | 3 | IREG_15125.14 | On (1) | Local | Remote | [8 empty] | Change events | Primary Detail | CNT_0000_Inv_[n]_HV_local_remote_switch_status
190 | Available | Counter | Inv [n] running | 32-bit bitfield | 0 | 4 | IREG_15116.0 | None | Running | Stopped | [8 empty] | Change events | KPI | CNT_0000_Inv_[n]_running
191 | Available | Counter | Inv [n] stopped | 32-bit bitfield | 0 | 5 | IREG_15116.1 | None | Stopped | Running | [8 empty] | Change events | KPI | CNT_0000_Inv_[n]_stopped
192 | Available | Counter | Inv [n] unit 1 status | 32-bit bitfield | 1 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0001_Inv_[n]_unit_1_status
193 | Available | Counter | Inv [n] unit 1 load switch status | 32-bit bitfield | 1 | 0 | IREG_15113.8 | None | Open | Closed | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_load_switch_status
194 | Available | Counter | Inv [n] unit 1 circuit breaker status | 32-bit bitfield | 1 | 1 | IREG_15193.0 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_circuit_breaker_status
195 | Available | Counter | Inv [n] unit 1 main contactor status | 32-bit bitfield | 1 | 2 | IREG_15193.1 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_main_contactor_status
196 | Available | Counter | Inv [n] unit 1 SPD status | 32-bit bitfield | 1 | 3 | IREG_15195.12 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_SPD_status
197 | Available | Counter | Inv [n] unit 1 DC switch 1 status | 32-bit bitfield | 1 | 4 | IREG_15195.20 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_DC_switch_1_status
198 | Available | Counter | Inv [n] unit 1 DC switch 2 status | 32-bit bitfield | 1 | 5 | IREG_15195.21 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_DC_switch_2_status
199 | Available | Counter | Inv [n] unit 1 DC switch 3 status | 32-bit bitfield | 1 | 6 | IREG_15195.22 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_DC_switch_3_status
200 | Available | Counter | Inv [n] unit 1 DC switch 4 status | 32-bit bitfield | 1 | 7 | IREG_15195.23 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_DC_switch_4_status
201 | Available | Counter | Inv [n] unit 1 running | 32-bit bitfield | 1 | 8 | IREG_15207.0 | None | Running | Not Running | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_running
202 | Available | Counter | Inv [n] unit 1 stopped | 32-bit bitfield | 1 | 9 | IREG_15207.1 | None | Stopped | Not Stopped | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_stopped
203 | Available | Counter | Inv [n] unit 1 initial standby | 32-bit bitfield | 1 | 10 | IREG_15207.2 | None | Standby | Not Standby | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_initial_standby
204 | Available | Counter | Inv [n] unit 1 key stop | 32-bit bitfield | 1 | 11 | IREG_15207.3 | None | Stopped | Not Stopped | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_key_stop
205 | Available | Counter | Inv [n] unit 1 standby | 32-bit bitfield | 1 | 12 | IREG_15207.4 | None | Standby | Not Standby | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_standby
206 | Available | Counter | Inv [n] unit 1 emergency stop | 32-bit bitfield | 1 | 13 | IREG_15207.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_emergency_stop
207 | Available | Counter | Inv [n] unit 1 starting | 32-bit bitfield | 1 | 14 | IREG_15207.6 | None | Starting | Not Starting | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_starting
208 | Available | Counter | Inv [n] unit 1 stopping | 32-bit bitfield | 1 | 15 | IREG_15207.7 | None | Stopping | Not Stopping | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_stopping
209 | Available | Counter | Inv [n] unit 1 fault stop | 32-bit bitfield | 1 | 16 | IREG_15207.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_fault_stop
210 | Available | Counter | Inv [n] unit 1 alarm running | 32-bit bitfield | 1 | 17 | IREG_15207.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_alarm_running
211 | Available | Counter | Inv [n] unit 1 derating running | 32-bit bitfield | 1 | 18 | IREG_15207.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_derating_running
212 | Available | Counter | Inv [n] unit 1 inverter is running | 32-bit bitfield | 1 | 19 | IREG_15207.17 | None | Running | Not Running | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_inverter_is_running
213 | Available | Counter | Inv [n] unit 1 inverter is stopped | 32-bit bitfield | 1 | 20 | IREG_15207.18 | None | Stopped | Not Stopped | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_inverter_is_stopped
214 | Available | Counter | Inv [n] unit 1 anti PID active | 32-bit bitfield | 1 | 21 | IREG_15207.19 | None | Active | Not-Active | [8 empty] | Change events | Diagnostic | CNT_0001_Inv_[n]_unit_1_anti_PID_active
215 | Available | Counter | Inv [n] unit 1 ABC local remote status | 32-bit bitfield | 1 | 22 | IREG_15193.13 | Off (0) | Remote | Local | [8 empty] | Change events | Primary Detail | CNT_0001_Inv_[n]_unit_1_ABC_local_remote_status
216 | Available | Counter | Inv [n] unit 2 status | 32-bit bitfield | 2 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0002_Inv_[n]_unit_2_status
217 | Available | Counter | Inv [n] unit 2 load switch status | 32-bit bitfield | 2 | 0 | IREG_15113.9 | None | Open | Closed | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_load_switch_status
218 | Available | Counter | Inv [n] unit 2 circuit breaker status | 32-bit bitfield | 2 | 1 | IREG_15313.0 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_circuit_breaker_status
219 | Available | Counter | Inv [n] unit 2 main contactor status | 32-bit bitfield | 2 | 2 | IREG_15313.1 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_main_contactor_status
220 | Available | Counter | Inv [n] unit 2 SPD status | 32-bit bitfield | 2 | 3 | IREG_15315.12 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_SPD_status
221 | Available | Counter | Inv [n] unit 2 DC switch 1 status | 32-bit bitfield | 2 | 4 | IREG_15315.20 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_DC_switch_1_status
222 | Available | Counter | Inv [n] unit 2 DC switch 2 status | 32-bit bitfield | 2 | 5 | IREG_15315.21 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_DC_switch_2_status
223 | Available | Counter | Inv [n] unit 2 DC switch 3 status | 32-bit bitfield | 2 | 6 | IREG_15315.22 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_DC_switch_3_status
224 | Available | Counter | Inv [n] unit 2 DC switch 4 status | 32-bit bitfield | 2 | 7 | IREG_15315.23 | None | Closed | Open | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_DC_switch_4_status
225 | Available | Counter | Inv [n] unit 2 running | 32-bit bitfield | 2 | 8 | IREG_15327.0 | None | Running | Not Running | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_running
226 | Available | Counter | Inv [n] unit 2 stopped | 32-bit bitfield | 2 | 9 | IREG_15327.1 | None | Stopped | Not Stopped | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_stopped
227 | Available | Counter | Inv [n] unit 2 initial standby | 32-bit bitfield | 2 | 10 | IREG_15327.2 | None | Standby | Not Standby | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_initial_standby
228 | Available | Counter | Inv [n] unit 2 key stop | 32-bit bitfield | 2 | 11 | IREG_15327.3 | None | Stopped | Not Stopped | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_key_stop
229 | Available | Counter | Inv [n] unit 2 standby | 32-bit bitfield | 2 | 12 | IREG_15327.4 | None | Standby | Not Standby | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_standby
230 | Available | Counter | Inv [n] unit 2 emergency stop | 32-bit bitfield | 2 | 13 | IREG_15327.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_emergency_stop
231 | Available | Counter | Inv [n] unit 2 starting | 32-bit bitfield | 2 | 14 | IREG_15327.6 | None | Starting | Not Starting | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_starting
232 | Available | Counter | Inv [n] unit 2 stopping | 32-bit bitfield | 2 | 15 | IREG_15327.7 | None | Stopping | Not Stopping | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_stopping
233 | Available | Counter | Inv [n] unit 2 fault stop | 32-bit bitfield | 2 | 16 | IREG_15327.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_fault_stop
234 | Available | Counter | Inv [n] unit 2 alarm running | 32-bit bitfield | 2 | 17 | IREG_15327.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_alarm_running
235 | Available | Counter | Inv [n] unit 2 derating running | 32-bit bitfield | 2 | 18 | IREG_15327.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_derating_running
236 | Available | Counter | Inv [n] unit 2 inverter is running | 32-bit bitfield | 2 | 19 | IREG_15327.17 | None | Running | Not Running | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_inverter_is_running
237 | Available | Counter | Inv [n] unit 2 inverter is stopped | 32-bit bitfield | 2 | 20 | IREG_15327.18 | None | Stopped | Not Stopped | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_inverter_is_stopped
238 | Available | Counter | Inv [n] unit 2 anti PID active | 32-bit bitfield | 2 | 21 | IREG_15327.19 | None | Active | Not-Active | [8 empty] | Change events | Diagnostic | CNT_0002_Inv_[n]_unit_2_anti_PID_active
239 | Available | Counter | Inv [n] unit 2 ABC local remote status | 32-bit bitfield | 2 | 22 | IREG_15313.13 | Off (0) | Remote | Local | [8 empty] | Change events | Primary Detail | CNT_0002_Inv_[n]_unit_2_ABC_local_remote_status
240 | Available | Counter | Inv [n] alarms | 32-bit bitfield | 3 |  | PPC Logic | None | [10 empty] | Change events | Not Shown | CNT_0003_Inv_[n]_alarms
241 | Available | Counter | Inv [n] overcurrent protection trip | 32-bit bitfield | 3 | 0 | IREG_15113.12 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_overcurrent_protection_trip
242 | Available | Counter | Inv [n] external emergency stop overall | 32-bit bitfield | 3 | 1 | IREG_15116.2 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_external_emergency_stop_overall
243 | Available | Counter | Inv [n] remote emergency stop | 32-bit bitfield | 3 | 2 | IREG_15116.3 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_remote_emergency_stop
244 | Available | Counter | Inv [n] local emergency stop | 32-bit bitfield | 3 | 3 | IREG_15116.6 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_local_emergency_stop
245 | Available | Counter | Inv [n] external emergency stop mv node | 32-bit bitfield | 3 | 4 | IREG_15125.11 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_external_emergency_stop_mv_node
246 | Available | Counter | Inv [n] door opening protection | 32-bit bitfield | 3 | 5 | IREG_15116.4 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_door_opening_protection
247 | Available | Counter | Inv [n] smoke alarm trip | 32-bit bitfield | 3 | 6 | IREG_15116.5 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_smoke_alarm_trip
248 | Available | Counter | Inv [n] HV compartment door open | 32-bit bitfield | 3 | 7 | IREG_15125.6 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_HV_compartment_door_open
249 | Available | Counter | Inv [n] SF6 low pressure | 32-bit bitfield | 3 | 8 | IREG_15125.10 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_SF6_low_pressure
250 | Available | Counter | Inv [n] MV fuse failure | 32-bit bitfield | 3 | 9 | IREG_15125.12 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_MV_fuse_failure
251 | Available | Counter | Inv [n] HV compartment smoke alarm | 32-bit bitfield | 3 | 10 | IREG_15125.13 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_HV_compartment_smoke_alarm
252 | Available | Counter | Inv [n] smoke sensor abnormal | 32-bit bitfield | 3 | 11 | IREG_15126.0 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_smoke_sensor_abnormal
253 | Available | Counter | Inv [n] temperature sensor abnormal | 32-bit bitfield | 3 | 12 | IREG_15126.3 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_temperature_sensor_abnormal
254 | Available | Counter | Inv [n] HV remote trip | 32-bit bitfield | 3 | 13 | IREG_15130.1 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_HV_remote_trip
255 | Available | Counter | Inv [n] UPS fault | 32-bit bitfield | 3 | 14 | IREG_15130.9 | On (1) | Tripped | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_UPS_fault
256 | Available | Counter | Inv [n] transformer alarms | 32-bit bitfield | 4 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0004_Inv_[n]_transformer_alarms
257 | Available | Counter | Inv [n] transformer gas buildup alarm | 32-bit bitfield | 4 | 0 | IREG_15113.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_gas_buildup_alarm
258 | Available | Counter | Inv [n] transformer gas buildup trip | 32-bit bitfield | 4 | 1 | IREG_15113.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_gas_buildup_trip
259 | Available | Counter | Inv [n] transformer oil temperature alarm | 32-bit bitfield | 4 | 2 | IREG_15113.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_oil_temperature_alarm
260 | Available | Counter | Inv [n] transformer oil temperature trip | 32-bit bitfield | 4 | 3 | IREG_15113.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_oil_temperature_trip
261 | Available | Counter | Inv [n] transformer low oil level alarm | 32-bit bitfield | 4 | 4 | IREG_15113.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_low_oil_level_alarm
262 | Available | Counter | Inv [n] transformer low oil level trip | 32-bit bitfield | 4 | 5 | IREG_15113.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_low_oil_level_trip
263 | Available | Counter | Inv [n] transformer high oil level alarm | 32-bit bitfield | 4 | 6 | IREG_15113.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_high_oil_level_alarm
264 | Available | Counter | Inv [n] transformer pressure relief valve alarm | 32-bit bitfield | 4 | 7 | IREG_15113.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_pressure_relief_valve_alarm
265 | Available | Counter | Inv [n] transformer pressure relief valve trip | 32-bit bitfield | 4 | 8 | IREG_15113.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_pressure_relief_valve_trip
266 | Available | Counter | Inv [n] transformer compartment door alarm | 32-bit bitfield | 4 | 9 | IREG_15130.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_compartment_door_alarm
267 | Available | Counter | Inv [n] transformer compartment smoke alarm | 32-bit bitfield | 4 | 10 | IREG_15130.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_transformer_compartment_smoke_alarm
268 | Available | Counter | Inv [n] unit 1 transformer over temperature alarm | 32-bit bitfield | 4 | 11 | IREG_15185.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_unit_1_transformer_over_temperature_alarm
269 | Available | Counter | Inv [n] unit 2 transformer over temperature alarm | 32-bit bitfield | 4 | 12 | IREG_15305.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0004_Inv_[n]_unit_2_transformer_over_temperature_alarm
270 | Available | Counter | Inv [n] unit 1 alarms 1 | 32-bit bitfield | 5 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0005_Inv_[n]_unit_1_alarms_1
271 | Available | Counter | Inv [n] unit 1 AC current imballance | 32-bit bitfield | 5 | 0 | IREG_15188.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_current_imballance
272 | Available | Counter | Inv [n] unit 1 AC fuse fault | 32-bit bitfield | 5 | 1 | IREG_15188.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_fuse_fault
273 | Available | Counter | Inv [n] unit 1 AC leakage current protection alarm | 32-bit bitfield | 5 | 2 | IREG_15186.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_leakage_current_protection_alarm
274 | Available | Counter | Inv [n] unit 1 AC overcurrent | 32-bit bitfield | 5 | 3 | IREG_15186.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_overcurrent
275 | Available | Counter | Inv [n] unit 1 AC overvoltage alarm | 32-bit bitfield | 5 | 4 | IREG_15186.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_overvoltage_alarm
276 | Available | Counter | Inv [n] unit 1 AC SPD fault | 32-bit bitfield | 5 | 5 | IREG_15188.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_SPD_fault
277 | Available | Counter | Inv [n] unit 1 AC SPD fault | 32-bit bitfield | 5 | 6 | IREG_15210.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_SPD_fault
278 | Available | Counter | Inv [n] unit 1 AC undervoltage alarm | 32-bit bitfield | 5 | 7 | IREG_15186.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_AC_undervoltage_alarm
279 | Available | Counter | Inv [n] unit 1 Anti islanding protection active | 32-bit bitfield | 5 | 8 | IREG_15186.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Anti_islanding_protection_active
280 | Available | Counter | Inv [n] unit 1 Bus overvoltage | 32-bit bitfield | 5 | 9 | IREG_15186.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Bus_overvoltage
281 | Available | Counter | Inv [n] unit 1 Bus undervoltage | 32-bit bitfield | 5 | 10 | IREG_15186.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Bus_undervoltage
282 | Available | Counter | Inv [n] unit 1 CT unbalance | 32-bit bitfield | 5 | 11 | IREG_15210.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_CT_unbalance
283 | Available | Counter | Inv [n] unit 1 Frequency abnormal | 32-bit bitfield | 5 | 12 | IREG_15186.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Frequency_abnormal
284 | Available | Counter | Inv [n] unit 1 Frequency abnormal | 32-bit bitfield | 5 | 13 | IREG_15210.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Frequency_abnormal
285 | Available | Counter | Inv [n] unit 1 Frequency deviation active power regulation | 32-bit bitfield | 5 | 14 | IREG_15210.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Frequency_deviation_active_power_regulation
286 | Available | Counter | Inv [n] unit 1 Grid voltage imballance | 32-bit bitfield | 5 | 15 | IREG_15188.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Grid_voltage_imballance
287 | Available | Counter | Inv [n] unit 1 Overfrequency alarm | 32-bit bitfield | 5 | 16 | IREG_15186.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Overfrequency_alarm
288 | Available | Counter | Inv [n] unit 1 Underfrequency alarm | 32-bit bitfield | 5 | 17 | IREG_15186.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Underfrequency_alarm
289 | Available | Counter | Inv [n] unit 1 Sampling fault | 32-bit bitfield | 5 | 18 | IREG_15188.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Sampling_fault
290 | Available | Counter | Inv [n] unit 1 Voltage deviation reactive power regulation | 32-bit bitfield | 5 | 19 | IREG_15210.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Voltage_deviation_reactive_power_regulation
291 | Available | Counter | Inv [n] unit 1 Current unbalance 2 | 32-bit bitfield | 5 | 20 | IREG_15188.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Current_unbalance_2
292 | Available | Counter | Inv [n] unit 1 Current unbalance 3 | 32-bit bitfield | 5 | 21 | IREG_15188.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_Current_unbalance_3
293 | Available | Counter | Inv [n] unit 1 DC bypass forward overcurrent alarm | 32-bit bitfield | 5 | 22 | IREG_15210.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_bypass_forward_overcurrent_alarm
294 | Available | Counter | Inv [n] unit 1 DC bypass reverse overcurrent alarm | 32-bit bitfield | 5 | 23 | IREG_15210.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_bypass_reverse_overcurrent_alarm
295 | Available | Counter | Inv [n] unit 1 DC fuse failure | 32-bit bitfield | 5 | 24 | IREG_15186.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_fuse_failure
296 | Available | Counter | Inv [n] unit 1 DC fuse failure | 32-bit bitfield | 5 | 25 | IREG_15210.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_fuse_failure
297 | Available | Counter | Inv [n] unit 1 DC fuse grounding fault | 32-bit bitfield | 5 | 26 | IREG_15188.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_fuse_grounding_fault
298 | Available | Counter | Inv [n] unit 1 DC injection fault | 32-bit bitfield | 5 | 27 | IREG_15188.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_injection_fault
299 | Available | Counter | Inv [n] unit 1 DC leakage current protection alarm | 32-bit bitfield | 5 | 28 | IREG_15186.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_leakage_current_protection_alarm
300 | Available | Counter | Inv [n] unit 1 DC overcurrent | 32-bit bitfield | 5 | 29 | IREG_15186.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_overcurrent
301 | Available | Counter | Inv [n] unit 1 DC overvoltage alarm | 32-bit bitfield | 5 | 30 | IREG_15186.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_overvoltage_alarm
302 | Available | Counter | Inv [n] unit 1 DC polarity reversed alarm | 32-bit bitfield | 5 | 31 | IREG_15188.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0005_Inv_[n]_unit_1_DC_polarity_reversed_alarm
303 | Available | Counter | Inv [n] unit 1 alarms 2 | 32-bit bitfield | 6 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0006_Inv_[n]_unit_1_alarms_2
304 | Available | Counter | Inv [n] unit 1 DC sensor fault | 32-bit bitfield | 6 | 0 | IREG_15210.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_sensor_fault
305 | Available | Counter | Inv [n] unit 1 DC SPD fault | 32-bit bitfield | 6 | 1 | IREG_15188.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_SPD_fault
306 | Available | Counter | Inv [n] unit 1 DC SPD fault | 32-bit bitfield | 6 | 2 | IREG_15210.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_SPD_fault
307 | Available | Counter | Inv [n] unit 1 DC switch fault | 32-bit bitfield | 6 | 3 | IREG_15188.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_switch_fault
308 | Available | Counter | Inv [n] unit 1 DC undervoltage alarm | 32-bit bitfield | 6 | 4 | IREG_15186.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_undervoltage_alarm
309 | Available | Counter | Inv [n] unit 1 Detection fuse failure | 32-bit bitfield | 6 | 5 | IREG_15186.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Detection_fuse_failure
310 | Available | Counter | Inv [n] unit 1 Insulation impedance fault | 32-bit bitfield | 6 | 6 | IREG_15188.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Insulation_impedance_fault
311 | Available | Counter | Inv [n] unit 1 Inverter overvoltage | 32-bit bitfield | 6 | 7 | IREG_15186.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Inverter_overvoltage
312 | Available | Counter | Inv [n] unit 1 Low insulation resistance alarm | 32-bit bitfield | 6 | 8 | IREG_15210.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Low_insulation_resistance_alarm
313 | Available | Counter | Inv [n] unit 1 Neutral point potential shift alarm | 32-bit bitfield | 6 | 9 | IREG_15188.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Neutral_point_potential_shift_alarm
314 | Available | Counter | Inv [n] unit 1 Temperature abnormal | 32-bit bitfield | 6 | 10 | IREG_15186.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Temperature_abnormal
315 | Available | Counter | Inv [n] unit 1 Temperature alarm | 32-bit bitfield | 6 | 11 | IREG_15210.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Temperature_alarm
316 | Available | Counter | Inv [n] unit 1 AC cabinet temperature alarm | 32-bit bitfield | 6 | 12 | IREG_15188.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_AC_cabinet_temperature_alarm
317 | Available | Counter | Inv [n] unit 1 DC cabinet temperature alarm | 32-bit bitfield | 6 | 13 | IREG_15188.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_cabinet_temperature_alarm
318 | Available | Counter | Inv [n] unit 1 Control cabinet temperature alarm | 32-bit bitfield | 6 | 14 | IREG_15188.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Control_cabinet_temperature_alarm
319 | Available | Counter | Inv [n] unit 1 Busbar temperature alarm | 32-bit bitfield | 6 | 15 | IREG_15210.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Busbar_temperature_alarm
320 | Available | Counter | Inv [n] unit 1 Module overtemperature alarm | 32-bit bitfield | 6 | 16 | IREG_15186.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Module_overtemperature_alarm
321 | Available | Counter | Inv [n] unit 1 Reactor overtemperature alarm | 32-bit bitfield | 6 | 17 | IREG_15186.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Reactor_overtemperature_alarm
322 | Available | Counter | Inv [n] unit 1 AC circuit breaker fault | 32-bit bitfield | 6 | 18 | IREG_15210.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_AC_circuit_breaker_fault
323 | Available | Counter | Inv [n] unit 1 Bypass circuit breaker fault | 32-bit bitfield | 6 | 19 | IREG_15210.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Bypass_circuit_breaker_fault
324 | Available | Counter | Inv [n] unit 1 AC switch fault | 32-bit bitfield | 6 | 20 | IREG_15188.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_AC_switch_fault
325 | Available | Counter | Inv [n] unit 1 AC switch disconnection | 32-bit bitfield | 6 | 21 | IREG_15188.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_AC_switch_disconnection
326 | Available | Counter | Inv [n] unit 1 DC switch fault | 32-bit bitfield | 6 | 22 | IREG_15210.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_DC_switch_fault
327 | Available | Counter | Inv [n] unit 1 Buffer contactor fault | 32-bit bitfield | 6 | 23 | IREG_15188.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Buffer_contactor_fault
328 | Available | Counter | Inv [n] unit 1 Contactor fault | 32-bit bitfield | 6 | 24 | IREG_15186.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Contactor_fault
329 | Available | Counter | Inv [n] unit 1 Contactor contact fault | 32-bit bitfield | 6 | 25 | IREG_15210.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Contactor_contact_fault
330 | Available | Counter | Inv [n] unit 1 Anti-PID power supply | 32-bit bitfield | 6 | 26 | IREG_15210.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Anti_PID_power_supply
331 | Available | Counter | Inv [n] unit 1 Backup power supply fault | 32-bit bitfield | 6 | 27 | IREG_15188.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Backup_power_supply_fault
332 | Available | Counter | Inv [n] unit 1 Control power supply fault | 32-bit bitfield | 6 | 28 | IREG_15188.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Control_power_supply_fault
333 | Available | Counter | Inv [n] unit 1 Bypass fuse abnormal / branch fault | 32-bit bitfield | 6 | 29 | IREG_15210.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Bypass_fuse_abnormal___branch_fault
334 | Available | Counter | Inv [n] unit 1 Ground fuse fault | 32-bit bitfield | 6 | 30 | IREG_15210.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Ground_fuse_fault
335 | Available | Counter | Inv [n] unit 1 Abnormal derating of fan | 32-bit bitfield | 6 | 31 | IREG_15210.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0006_Inv_[n]_unit_1_Abnormal_derating_of_fan
336 | Available | Counter | Inv [n] unit 1 alarms 3 | 32-bit bitfield | 7 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0007_Inv_[n]_unit_1_alarms_3
337 | Available | Counter | Inv [n] unit 1 Fan fault | 32-bit bitfield | 7 | 0 | IREG_15186.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Fan_fault
338 | Available | Counter | Inv [n] unit 1 Fan fault | 32-bit bitfield | 7 | 1 | IREG_15210.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Fan_fault
339 | Available | Counter | Inv [n] unit 1 Fan 2 fault | 32-bit bitfield | 7 | 2 | IREG_15188.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Fan_2_fault
340 | Available | Counter | Inv [n] unit 1 Fan 2 fault | 32-bit bitfield | 7 | 3 | IREG_15210.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Fan_2_fault
341 | Available | Counter | Inv [n] unit 1 Grounding fault | 32-bit bitfield | 7 | 4 | IREG_15186.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Grounding_fault
342 | Available | Counter | Inv [n] unit 1 Drive board fault | 32-bit bitfield | 7 | 5 | IREG_15188.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Drive_board_fault
343 | Available | Counter | Inv [n] unit 1 Hardware fault | 32-bit bitfield | 7 | 6 | IREG_15186.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Hardware_fault
344 | Available | Counter | Inv [n] unit 1 Insulation impedance sensor fault | 32-bit bitfield | 7 | 7 | IREG_15210.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Insulation_impedance_sensor_fault
345 | Available | Counter | Inv [n] unit 1 Sensor failure | 32-bit bitfield | 7 | 8 | IREG_15186.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Sensor_failure
346 | Available | Counter | Inv [n] unit 1 Temperature and humidity sensor fault | 32-bit bitfield | 7 | 9 | IREG_15210.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Temperature_and_humidity_sensor_fault
347 | Available | Counter | Inv [n] unit 1 DC voltage sampling fault | 32-bit bitfield | 7 | 10 | IREG_15188.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_DC_voltage_sampling_fault
348 | Available | Counter | Inv [n] unit 1 Soft start fault | 32-bit bitfield | 7 | 11 | IREG_15188.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Soft_start_fault
349 | Available | Counter | Inv [n] unit 1 DSP-MDC communication failure | 32-bit bitfield | 7 | 12 | IREG_15210.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_DSP_MDC_communication_failure
350 | Available | Counter | Inv [n] unit 1 IO-DSP communication failure | 32-bit bitfield | 7 | 13 | IREG_15208.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_IO_DSP_communication_failure
351 | Available | Counter | Inv [n] unit 1 IO-MDC communication abnormal | 32-bit bitfield | 7 | 14 | IREG_15208.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_IO_MDC_communication_abnormal
352 | Available | Counter | Inv [n] unit 1 Meter communication failure | 32-bit bitfield | 7 | 15 | IREG_15210.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Meter_communication_failure
353 | Available | Counter | Inv [n] unit 1 Parallel operation communication failure | 32-bit bitfield | 7 | 16 | IREG_15188.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Parallel_operation_communication_failure
354 | Available | Counter | Inv [n] unit 1 Tributary board communication failure | 32-bit bitfield | 7 | 17 | IREG_15210.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Tributary_board_communication_failure
355 | Available | Counter | Inv [n] unit 1 ABC fault | 32-bit bitfield | 7 | 18 | IREG_15194.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_ABC_fault
356 | Available | Counter | Inv [n] unit 1 Carrier sync failure | 32-bit bitfield | 7 | 19 | IREG_15188.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Carrier_sync_failure
357 | Available | Counter | Inv [n] unit 1 Device code repeat fault | 32-bit bitfield | 7 | 20 | IREG_15188.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Device_code_repeat_fault
358 | Available | Counter | Inv [n] unit 1 External power supply fault | 32-bit bitfield | 7 | 21 | IREG_15210.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_External_power_supply_fault
359 | Available | Counter | Inv [n] unit 1 GFDI protection active | 32-bit bitfield | 7 | 22 | IREG_15186.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_GFDI_protection_active
360 | Available | Counter | Inv [n] unit 1 GFRT operation alarm | 32-bit bitfield | 7 | 23 | IREG_15210.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_GFRT_operation_alarm
361 | Available | Counter | Inv [n] unit 1 Overload protection active | 32-bit bitfield | 7 | 24 | IREG_15186.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Overload_protection_active
362 | Available | Counter | Inv [n] unit 1 PDP protection active | 32-bit bitfield | 7 | 25 | IREG_15186.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_PDP_protection_active
363 | Available | Counter | Inv [n] unit 1 Reversed branch over current | 32-bit bitfield | 7 | 26 | IREG_15188.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0007_Inv_[n]_unit_1_Reversed_branch_over_current
364 | Available | Counter | Inv [n] unit 2 alarms 1 | 32-bit bitfield | 8 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0008_Inv_[n]_unit_2_alarms_1
365 | Available | Counter | Inv [n] unit 2 AC current imballance | 32-bit bitfield | 8 | 0 | IREG_15188.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_current_imballance
366 | Available | Counter | Inv [n] unit 2 AC fuse fault | 32-bit bitfield | 8 | 1 | IREG_15188.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_fuse_fault
367 | Available | Counter | Inv [n] unit 2 AC leakage current protection alarm | 32-bit bitfield | 8 | 2 | IREG_15186.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_leakage_current_protection_alarm
368 | Available | Counter | Inv [n] unit 2 AC overcurrent | 32-bit bitfield | 8 | 3 | IREG_15186.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_overcurrent
369 | Available | Counter | Inv [n] unit 2 AC overvoltage alarm | 32-bit bitfield | 8 | 4 | IREG_15186.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_overvoltage_alarm
370 | Available | Counter | Inv [n] unit 2 AC SPD fault | 32-bit bitfield | 8 | 5 | IREG_15188.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_SPD_fault
371 | Available | Counter | Inv [n] unit 2 AC SPD fault | 32-bit bitfield | 8 | 6 | IREG_15210.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_SPD_fault
372 | Available | Counter | Inv [n] unit 2 AC undervoltage alarm | 32-bit bitfield | 8 | 7 | IREG_15186.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_AC_undervoltage_alarm
373 | Available | Counter | Inv [n] unit 2 Anti islanding protection active | 32-bit bitfield | 8 | 8 | IREG_15186.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Anti_islanding_protection_active
374 | Available | Counter | Inv [n] unit 2 Bus overvoltage | 32-bit bitfield | 8 | 9 | IREG_15186.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Bus_overvoltage
375 | Available | Counter | Inv [n] unit 2 Bus undervoltage | 32-bit bitfield | 8 | 10 | IREG_15186.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Bus_undervoltage
376 | Available | Counter | Inv [n] unit 2 CT unbalance | 32-bit bitfield | 8 | 11 | IREG_15210.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_CT_unbalance
377 | Available | Counter | Inv [n] unit 2 Frequency abnormal | 32-bit bitfield | 8 | 12 | IREG_15186.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Frequency_abnormal
378 | Available | Counter | Inv [n] unit 2 Frequency abnormal | 32-bit bitfield | 8 | 13 | IREG_15210.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Frequency_abnormal
379 | Available | Counter | Inv [n] unit 2 Frequency deviation active power regulation | 32-bit bitfield | 8 | 14 | IREG_15210.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Frequency_deviation_active_power_regulation
380 | Available | Counter | Inv [n] unit 2 Grid voltage imballance | 32-bit bitfield | 8 | 15 | IREG_15188.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Grid_voltage_imballance
381 | Available | Counter | Inv [n] unit 2 Overfrequency alarm | 32-bit bitfield | 8 | 16 | IREG_15186.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Overfrequency_alarm
382 | Available | Counter | Inv [n] unit 2 Underfrequency alarm | 32-bit bitfield | 8 | 17 | IREG_15186.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Underfrequency_alarm
383 | Available | Counter | Inv [n] unit 2 Sampling fault | 32-bit bitfield | 8 | 18 | IREG_15188.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Sampling_fault
384 | Available | Counter | Inv [n] unit 2 Voltage deviation reactive power regulation | 32-bit bitfield | 8 | 19 | IREG_15210.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Voltage_deviation_reactive_power_regulation
385 | Available | Counter | Inv [n] unit 2 Current unbalance 2 | 32-bit bitfield | 8 | 20 | IREG_15188.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Current_unbalance_2
386 | Available | Counter | Inv [n] unit 2 Current unbalance 3 | 32-bit bitfield | 8 | 21 | IREG_15188.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_Current_unbalance_3
387 | Available | Counter | Inv [n] unit 2 DC bypass forward overcurrent alarm | 32-bit bitfield | 8 | 22 | IREG_15210.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_bypass_forward_overcurrent_alarm
388 | Available | Counter | Inv [n] unit 2 DC bypass reverse overcurrent alarm | 32-bit bitfield | 8 | 23 | IREG_15210.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_bypass_reverse_overcurrent_alarm
389 | Available | Counter | Inv [n] unit 2 DC fuse failure | 32-bit bitfield | 8 | 24 | IREG_15186.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_fuse_failure
390 | Available | Counter | Inv [n] unit 2 DC fuse failure | 32-bit bitfield | 8 | 25 | IREG_15210.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_fuse_failure
391 | Available | Counter | Inv [n] unit 2 DC fuse grounding fault | 32-bit bitfield | 8 | 26 | IREG_15188.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_fuse_grounding_fault
392 | Available | Counter | Inv [n] unit 2 DC injection fault | 32-bit bitfield | 8 | 27 | IREG_15188.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_injection_fault
393 | Available | Counter | Inv [n] unit 2 DC leakage current protection alarm | 32-bit bitfield | 8 | 28 | IREG_15186.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_leakage_current_protection_alarm
394 | Available | Counter | Inv [n] unit 2 DC overcurrent | 32-bit bitfield | 8 | 29 | IREG_15186.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_overcurrent
395 | Available | Counter | Inv [n] unit 2 DC overvoltage alarm | 32-bit bitfield | 8 | 30 | IREG_15186.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_overvoltage_alarm
396 | Available | Counter | Inv [n] unit 2 DC polarity reversed alarm | 32-bit bitfield | 8 | 31 | IREG_15188.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0008_Inv_[n]_unit_2_DC_polarity_reversed_alarm
397 | Available | Counter | Inv [n] unit 2 alarms 2 | 32-bit bitfield | 9 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0009_Inv_[n]_unit_2_alarms_2
398 | Available | Counter | Inv [n] unit 2 DC sensor fault | 32-bit bitfield | 9 | 0 | IREG_15329.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_sensor_fault
399 | Available | Counter | Inv [n] unit 2 DC SPD fault | 32-bit bitfield | 9 | 1 | IREG_15307.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_SPD_fault
400 | Available | Counter | Inv [n] unit 2 DC SPD fault | 32-bit bitfield | 9 | 2 | IREG_15329.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_SPD_fault
401 | Available | Counter | Inv [n] unit 2 DC switch fault | 32-bit bitfield | 9 | 3 | IREG_15307.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_switch_fault
402 | Available | Counter | Inv [n] unit 2 DC undervoltage alarm | 32-bit bitfield | 9 | 4 | IREG_15305.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_undervoltage_alarm
403 | Available | Counter | Inv [n] unit 2 Detection fuse failure | 32-bit bitfield | 9 | 5 | IREG_15305.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Detection_fuse_failure
404 | Available | Counter | Inv [n] unit 2 Insulation impedance fault | 32-bit bitfield | 9 | 6 | IREG_15307.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Insulation_impedance_fault
405 | Available | Counter | Inv [n] unit 2 Inverter overvoltage | 32-bit bitfield | 9 | 7 | IREG_15305.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Inverter_overvoltage
406 | Available | Counter | Inv [n] unit 2 Low insulation resistance alarm | 32-bit bitfield | 9 | 8 | IREG_15329.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Low_insulation_resistance_alarm
407 | Available | Counter | Inv [n] unit 2 Neutral point potential shift alarm | 32-bit bitfield | 9 | 9 | IREG_15307.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Neutral_point_potential_shift_alarm
408 | Available | Counter | Inv [n] unit 2 Temperature abnormal | 32-bit bitfield | 9 | 10 | IREG_15305.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Temperature_abnormal
409 | Available | Counter | Inv [n] unit 2 Temperature alarm | 32-bit bitfield | 9 | 11 | IREG_15329.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Temperature_alarm
410 | Available | Counter | Inv [n] unit 2 AC cabinet temperature alarm | 32-bit bitfield | 9 | 12 | IREG_15307.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_AC_cabinet_temperature_alarm
411 | Available | Counter | Inv [n] unit 2 DC cabinet temperature alarm | 32-bit bitfield | 9 | 13 | IREG_15307.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_cabinet_temperature_alarm
412 | Available | Counter | Inv [n] unit 2 Control cabinet temperature alarm | 32-bit bitfield | 9 | 14 | IREG_15307.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Control_cabinet_temperature_alarm
413 | Available | Counter | Inv [n] unit 2 Busbar temperature alarm | 32-bit bitfield | 9 | 15 | IREG_15329.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Busbar_temperature_alarm
414 | Available | Counter | Inv [n] unit 2 Module overtemperature alarm | 32-bit bitfield | 9 | 16 | IREG_15305.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Module_overtemperature_alarm
415 | Available | Counter | Inv [n] unit 2 Reactor overtemperature alarm | 32-bit bitfield | 9 | 17 | IREG_15305.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Reactor_overtemperature_alarm
416 | Available | Counter | Inv [n] unit 2 AC circuit breaker fault | 32-bit bitfield | 9 | 18 | IREG_15329.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_AC_circuit_breaker_fault
417 | Available | Counter | Inv [n] unit 2 Bypass circuit breaker fault | 32-bit bitfield | 9 | 19 | IREG_15329.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Bypass_circuit_breaker_fault
418 | Available | Counter | Inv [n] unit 2 AC switch fault | 32-bit bitfield | 9 | 20 | IREG_15307.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_AC_switch_fault
419 | Available | Counter | Inv [n] unit 2 AC switch disconnection | 32-bit bitfield | 9 | 21 | IREG_15307.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_AC_switch_disconnection
420 | Available | Counter | Inv [n] unit 2 DC switch fault | 32-bit bitfield | 9 | 22 | IREG_15329.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_DC_switch_fault
421 | Available | Counter | Inv [n] unit 2 Buffer contactor fault | 32-bit bitfield | 9 | 23 | IREG_15307.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Buffer_contactor_fault
422 | Available | Counter | Inv [n] unit 2 Contactor fault | 32-bit bitfield | 9 | 24 | IREG_15305.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Contactor_fault
423 | Available | Counter | Inv [n] unit 2 Contactor contact fault | 32-bit bitfield | 9 | 25 | IREG_15329.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Contactor_contact_fault
424 | Available | Counter | Inv [n] unit 2 Anti-PID power supply | 32-bit bitfield | 9 | 26 | IREG_15329.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Anti_PID_power_supply
425 | Available | Counter | Inv [n] unit 2 Backup power supply fault | 32-bit bitfield | 9 | 27 | IREG_15307.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Backup_power_supply_fault
426 | Available | Counter | Inv [n] unit 2 Control power supply fault | 32-bit bitfield | 9 | 28 | IREG_15307.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Control_power_supply_fault
427 | Available | Counter | Inv [n] unit 2 Bypass fuse abnormal / branch fault | 32-bit bitfield | 9 | 29 | IREG_15329.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Bypass_fuse_abnormal___branch_fault
428 | Available | Counter | Inv [n] unit 2 Ground fuse fault | 32-bit bitfield | 9 | 30 | IREG_15329.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Ground_fuse_fault
429 | Available | Counter | Inv [n] unit 2 Abnormal derating of fan | 32-bit bitfield | 9 | 31 | IREG_15329.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0009_Inv_[n]_unit_2_Abnormal_derating_of_fan
430 | Available | Counter | Inv [n] unit 2 alarms 3 | 32-bit bitfield | 10 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0010_Inv_[n]_unit_2_alarms_3
431 | Available | Counter | Inv [n] unit 2 Fan fault | 32-bit bitfield | 10 | 0 | IREG_15305.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Fan_fault
432 | Available | Counter | Inv [n] unit 2 Fan fault | 32-bit bitfield | 10 | 1 | IREG_15329.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Fan_fault
433 | Available | Counter | Inv [n] unit 2 Fan 2 fault | 32-bit bitfield | 10 | 2 | IREG_15307.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Fan_2_fault
434 | Available | Counter | Inv [n] unit 2 Fan 2 fault | 32-bit bitfield | 10 | 3 | IREG_15329.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Fan_2_fault
435 | Available | Counter | Inv [n] unit 2 Grounding fault | 32-bit bitfield | 10 | 4 | IREG_15305.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Grounding_fault
436 | Available | Counter | Inv [n] unit 2 Drive board fault | 32-bit bitfield | 10 | 5 | IREG_15307.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Drive_board_fault
437 | Available | Counter | Inv [n] unit 2 Hardware fault | 32-bit bitfield | 10 | 6 | IREG_15305.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Hardware_fault
438 | Available | Counter | Inv [n] unit 2 Insulation impedance sensor fault | 32-bit bitfield | 10 | 7 | IREG_15329.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Insulation_impedance_sensor_fault
439 | Available | Counter | Inv [n] unit 2 Sensor failure | 32-bit bitfield | 10 | 8 | IREG_15305.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Sensor_failure
440 | Available | Counter | Inv [n] unit 2 Temperature and humidity sensor fault | 32-bit bitfield | 10 | 9 | IREG_15329.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Temperature_and_humidity_sensor_fault
441 | Available | Counter | Inv [n] unit 2 DC voltage sampling fault | 32-bit bitfield | 10 | 10 | IREG_15307.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_DC_voltage_sampling_fault
442 | Available | Counter | Inv [n] unit 2 Soft start fault | 32-bit bitfield | 10 | 11 | IREG_15307.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Soft_start_fault
443 | Available | Counter | Inv [n] unit 2 DSP-MDC communication failure | 32-bit bitfield | 10 | 12 | IREG_15329.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_DSP_MDC_communication_failure
444 | Available | Counter | Inv [n] unit 2 IO-DSP communication failure | 32-bit bitfield | 10 | 13 | IREG_15327.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_IO_DSP_communication_failure
445 | Available | Counter | Inv [n] unit 2 IO-MDC communication abnormal | 32-bit bitfield | 10 | 14 | IREG_15327.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_IO_MDC_communication_abnormal
446 | Available | Counter | Inv [n] unit 2 Meter communication failure | 32-bit bitfield | 10 | 15 | IREG_15329.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Meter_communication_failure
447 | Available | Counter | Inv [n] unit 2 Parallel operation communication failure | 32-bit bitfield | 10 | 16 | IREG_15307.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Parallel_operation_communication_failure
448 | Available | Counter | Inv [n] unit 2 Tributary board communication failure | 32-bit bitfield | 10 | 17 | IREG_15329.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Tributary_board_communication_failure
449 | Available | Counter | Inv [n] unit 2 ABC fault | 32-bit bitfield | 10 | 18 | IREG_15313.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_ABC_fault
450 | Available | Counter | Inv [n] unit 2 Carrier sync failure | 32-bit bitfield | 10 | 19 | IREG_15307.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Carrier_sync_failure
451 | Available | Counter | Inv [n] unit 2 Device code repeat fault | 32-bit bitfield | 10 | 20 | IREG_15307.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Device_code_repeat_fault
452 | Available | Counter | Inv [n] unit 2 External power supply fault | 32-bit bitfield | 10 | 21 | IREG_15329.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_External_power_supply_fault
453 | Available | Counter | Inv [n] unit 2 GFDI protection active | 32-bit bitfield | 10 | 22 | IREG_15305.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_GFDI_protection_active
454 | Available | Counter | Inv [n] unit 2 GFRT operation alarm | 32-bit bitfield | 10 | 23 | IREG_15329.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_GFRT_operation_alarm
455 | Available | Counter | Inv [n] unit 2 Overload protection active | 32-bit bitfield | 10 | 24 | IREG_15305.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Overload_protection_active
456 | Available | Counter | Inv [n] unit 2 PDP protection active | 32-bit bitfield | 10 | 25 | IREG_15305.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_PDP_protection_active
457 | Available | Counter | Inv [n] unit 2 Reversed branch over current | 32-bit bitfield | 10 | 26 | IREG_15307.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0010_Inv_[n]_unit_2_Reversed_branch_over_current
458 | Available | Counter | Inv [n] zone monitor branch open circuit | 32-bit bitfield | 11 |  | IREG_16000 | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0011_Inv_[n]_zone_monitor_branch_open_circuit
459 | Available | Counter | Inv [n] unit 1 open circuit fault branch 1 | 32-bit bitfield | 11 | 0 | IREG_16000.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_1
460 | Available | Counter | Inv [n] unit 1 open circuit fault branch 2 | 32-bit bitfield | 11 | 1 | IREG_16000.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_2
461 | Available | Counter | Inv [n] unit 1 open circuit fault branch 3 | 32-bit bitfield | 11 | 2 | IREG_16000.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_3
462 | Available | Counter | Inv [n] unit 1 open circuit fault branch 4 | 32-bit bitfield | 11 | 3 | IREG_16000.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_4
463 | Available | Counter | Inv [n] unit 1 open circuit fault branch 5 | 32-bit bitfield | 11 | 4 | IREG_16000.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_5
464 | Available | Counter | Inv [n] unit 1 open circuit fault branch 6 | 32-bit bitfield | 11 | 5 | IREG_16000.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_6
465 | Available | Counter | Inv [n] unit 1 open circuit fault branch 7 | 32-bit bitfield | 11 | 6 | IREG_16000.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_7
466 | Available | Counter | Inv [n] unit 1 open circuit fault branch 8 | 32-bit bitfield | 11 | 7 | IREG_16000.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_8
467 | Available | Counter | Inv [n] unit 1 open circuit fault branch 9 | 32-bit bitfield | 11 | 8 | IREG_16000.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_9
468 | Available | Counter | Inv [n] unit 1 open circuit fault branch 10 | 32-bit bitfield | 11 | 9 | IREG_16000.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_10
469 | Available | Counter | Inv [n] unit 1 open circuit fault branch 11 | 32-bit bitfield | 11 | 10 | IREG_16000.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_11
470 | Available | Counter | Inv [n] unit 1 open circuit fault branch 12 | 32-bit bitfield | 11 | 11 | IREG_16000.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_12
471 | Available | Counter | Inv [n] unit 1 open circuit fault branch 13 | 32-bit bitfield | 11 | 12 | IREG_16000.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_13
472 | Available | Counter | Inv [n] unit 1 open circuit fault branch 14 | 32-bit bitfield | 11 | 13 | IREG_16000.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_14
473 | Available | Counter | Inv [n] unit 1 open circuit fault branch 15 | 32-bit bitfield | 11 | 14 | IREG_16000.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_15
474 | Available | Counter | Inv [n] unit 1 open circuit fault branch 16 | 32-bit bitfield | 11 | 15 | IREG_16000.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_open_circuit_fault_branch_16
475 | Available | Counter | Inv [n] unit 2 open circuit fault branch 1 | 32-bit bitfield | 11 | 16 | IREG_16000.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_1
476 | Available | Counter | Inv [n] unit 2 open circuit fault branch 2 | 32-bit bitfield | 11 | 17 | IREG_16000.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_2
477 | Available | Counter | Inv [n] unit 2 open circuit fault branch 3 | 32-bit bitfield | 11 | 18 | IREG_16000.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_3
478 | Available | Counter | Inv [n] unit 2 open circuit fault branch 4 | 32-bit bitfield | 11 | 19 | IREG_16000.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_4
479 | Available | Counter | Inv [n] unit 2 open circuit fault branch 5 | 32-bit bitfield | 11 | 20 | IREG_16000.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_5
480 | Available | Counter | Inv [n] unit 2 open circuit fault branch 6 | 32-bit bitfield | 11 | 21 | IREG_16000.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_6
481 | Available | Counter | Inv [n] unit 2 open circuit fault branch 7 | 32-bit bitfield | 11 | 22 | IREG_16000.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_7
482 | Available | Counter | Inv [n] unit 2 open circuit fault branch 8 | 32-bit bitfield | 11 | 23 | IREG_16000.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_8
483 | Available | Counter | Inv [n] unit 2 open circuit fault branch 9 | 32-bit bitfield | 11 | 24 | IREG_16000.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_9
484 | Available | Counter | Inv [n] unit 2 open circuit fault branch 10 | 32-bit bitfield | 11 | 25 | IREG_16000.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_10
485 | Available | Counter | Inv [n] unit 2 open circuit fault branch 11 | 32-bit bitfield | 11 | 26 | IREG_16000.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_11
486 | Available | Counter | Inv [n] unit 2 open circuit fault branch 12 | 32-bit bitfield | 11 | 27 | IREG_16000.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_12
487 | Available | Counter | Inv [n] unit 2 open circuit fault branch 13 | 32-bit bitfield | 11 | 28 | IREG_16000.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_13
488 | Available | Counter | Inv [n] unit 2 open circuit fault branch 14 | 32-bit bitfield | 11 | 29 | IREG_16000.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_14
489 | Available | Counter | Inv [n] unit 2 open circuit fault branch 15 | 32-bit bitfield | 11 | 30 | IREG_16000.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_15
490 | Available | Counter | Inv [n] unit 2 open circuit fault branch 16 | 32-bit bitfield | 11 | 31 | IREG_16000.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_2_open_circuit_fault_branch_16
491 | Available | Counter | Inv [n] zone monitor string failure | 32-bit bitfield | 12 |  | IREG_16002 | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0012_Inv_[n]_zone_monitor_string_failure
492 | Available | Counter | Inv [n] unit 1 string failure branch 1 | 32-bit bitfield | 12 | 0 | IREG_16002.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_1
493 | Available | Counter | Inv [n] unit 1 string failure branch 2 | 32-bit bitfield | 12 | 1 | IREG_16002.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_2
494 | Available | Counter | Inv [n] unit 1 string failure branch 3 | 32-bit bitfield | 12 | 2 | IREG_16002.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_3
495 | Available | Counter | Inv [n] unit 1 string failure branch 4 | 32-bit bitfield | 12 | 3 | IREG_16002.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_4
496 | Available | Counter | Inv [n] unit 1 string failure branch 5 | 32-bit bitfield | 12 | 4 | IREG_16002.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_5
497 | Available | Counter | Inv [n] unit 1 string failure branch 6 | 32-bit bitfield | 12 | 5 | IREG_16002.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_6
498 | Available | Counter | Inv [n] unit 1 string failure branch 7 | 32-bit bitfield | 12 | 6 | IREG_16002.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_7
499 | Available | Counter | Inv [n] unit 1 string failure branch 8 | 32-bit bitfield | 12 | 7 | IREG_16002.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_8
500 | Available | Counter | Inv [n] unit 1 string failure branch 9 | 32-bit bitfield | 12 | 8 | IREG_16002.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_9
501 | Available | Counter | Inv [n] unit 1 string failure branch 10 | 32-bit bitfield | 12 | 9 | IREG_16002.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_10
502 | Available | Counter | Inv [n] unit 1 string failure branch 11 | 32-bit bitfield | 12 | 10 | IREG_16002.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_11
503 | Available | Counter | Inv [n] unit 1 string failure branch 12 | 32-bit bitfield | 12 | 11 | IREG_16002.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_12
504 | Available | Counter | Inv [n] unit 1 string failure branch 13 | 32-bit bitfield | 12 | 12 | IREG_16002.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_13
505 | Available | Counter | Inv [n] unit 1 string failure branch 14 | 32-bit bitfield | 12 | 13 | IREG_16002.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_14
506 | Available | Counter | Inv [n] unit 1 string failure branch 15 | 32-bit bitfield | 12 | 14 | IREG_16002.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_15
507 | Available | Counter | Inv [n] unit 1 string failure branch 16 | 32-bit bitfield | 12 | 15 | IREG_16002.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_string_failure_branch_16
508 | Available | Counter | Inv [n] unit 2 string failure branch 1 | 32-bit bitfield | 12 | 16 | IREG_16002.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_1
509 | Available | Counter | Inv [n] unit 2 string failure branch 2 | 32-bit bitfield | 12 | 17 | IREG_16002.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_2
510 | Available | Counter | Inv [n] unit 2 string failure branch 3 | 32-bit bitfield | 12 | 18 | IREG_16002.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_3
511 | Available | Counter | Inv [n] unit 2 string failure branch 4 | 32-bit bitfield | 12 | 19 | IREG_16002.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_4
512 | Available | Counter | Inv [n] unit 2 string failure branch 5 | 32-bit bitfield | 12 | 20 | IREG_16002.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_5
513 | Available | Counter | Inv [n] unit 2 string failure branch 6 | 32-bit bitfield | 12 | 21 | IREG_16002.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_6
514 | Available | Counter | Inv [n] unit 2 string failure branch 7 | 32-bit bitfield | 12 | 22 | IREG_16002.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_7
515 | Available | Counter | Inv [n] unit 2 string failure branch 8 | 32-bit bitfield | 12 | 23 | IREG_16002.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_8
516 | Available | Counter | Inv [n] unit 2 string failure branch 9 | 32-bit bitfield | 12 | 24 | IREG_16002.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_9
517 | Available | Counter | Inv [n] unit 2 string failure branch 10 | 32-bit bitfield | 12 | 25 | IREG_16002.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_10
518 | Available | Counter | Inv [n] unit 2 string failure branch 11 | 32-bit bitfield | 12 | 26 | IREG_16002.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_11
519 | Available | Counter | Inv [n] unit 2 string failure branch 12 | 32-bit bitfield | 12 | 27 | IREG_16002.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_12
520 | Available | Counter | Inv [n] unit 2 string failure branch 13 | 32-bit bitfield | 12 | 28 | IREG_16002.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_13
521 | Available | Counter | Inv [n] unit 2 string failure branch 14 | 32-bit bitfield | 12 | 29 | IREG_16002.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_14
522 | Available | Counter | Inv [n] unit 2 string failure branch 15 | 32-bit bitfield | 12 | 30 | IREG_16002.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_15
523 | Available | Counter | Inv [n] unit 2 string failure branch 16 | 32-bit bitfield | 12 | 31 | IREG_16002.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_2_string_failure_branch_16
524 | Available | Counter | Inv [n] unit 1 fault state 1 register | 32-bit bitfield | 13 |  | IREG_15185 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0013_Inv_[n]_unit_1_fault_state_1_register
525 | Available | Counter | Inv [n] unit 1 fault state 2 register | 32-bit bitfield | 14 |  | IREG_15187 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0014_Inv_[n]_unit_1_fault_state_2_register
526 | Available | Counter | Inv [n] unit 1 node state 1 register | 32-bit bitfield | 15 |  | IREG_15193 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0015_Inv_[n]_unit_1_node_state_1_register
527 | Available | Counter | Inv [n] unit 1 node state 2 register | 32-bit bitfield | 16 |  | IREG_15195 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0016_Inv_[n]_unit_1_node_state_2_register
528 | Available | Counter | Inv [n] unit 1 work state register | 32-bit bitfield | 17 |  | IREG_15207 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0017_Inv_[n]_unit_1_work_state_register
529 | Available | Counter | Inv [n] unit 1 alarm state register | 32-bit bitfield | 18 |  | IREG_15209 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0018_Inv_[n]_unit_1_alarm_state_register
530 | Available | Counter | Inv [n] unit 2 fault state 1 register | 32-bit bitfield | 19 |  | IREG_15305 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0019_Inv_[n]_unit_2_fault_state_1_register
531 | Available | Counter | Inv [n] unit 2 fault state 2 register | 32-bit bitfield | 20 |  | IREG_15307 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0020_Inv_[n]_unit_2_fault_state_2_register
532 | Available | Counter | Inv [n] unit 2 node state 1 register | 32-bit bitfield | 21 |  | IREG_15313 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0021_Inv_[n]_unit_2_node_state_1_register
533 | Available | Counter | Inv [n] unit 2 node state 2 register | 32-bit bitfield | 22 |  | IREG_15315 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0022_Inv_[n]_unit_2_node_state_2_register
534 | Available | Counter | Inv [n] unit 2 work state register | 32-bit bitfield | 23 |  | IREG_15327 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0023_Inv_[n]_unit_2_work_state_register
535 | Available | Counter | Inv [n] unit 2 alarm state register | 32-bit bitfield | 24 |  | IREG_15329 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0024_Inv_[n]_unit_2_alarm_state_register
536 | Available | Counter | Inv [n] transformer node state register | 32-bit bitfield | 25 |  | IREG_15113 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0025_Inv_[n]_transformer_node_state_register
537 | Available | Counter | Inv [n] overall work state register | 32-bit bitfield | 26 |  | IREG_15116 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0026_Inv_[n]_overall_work_state_register
538 | Available | Counter | Inv [n] mv node 1 state register | 32-bit bitfield | 27 |  | IREG_15125 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0027_Inv_[n]_mv_node_1_state_register
539 | Available | Counter | Inv [n] mv node 2 state register | 32-bit bitfield | 28 |  | IREG_15130 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0028_Inv_[n]_mv_node_2_state_register
540 | Available | Counter | Inv [n] overall alarm state register | 32-bit bitfield | 29 |  | IREG_15126 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0029_Inv_[n]_overall_alarm_state_register
541 | Available | Counter | Inv [n] digital input state register | 32-bit bitfield | 30 |  | IREG_15128 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0030_Inv_[n]_digital_input_state_register
542 | Available | Binary input | Inv [n] any alarm | Boolean | 0 |  | PPC Logic | None | Alarm | Normal | [8 empty] | Change events | KPI | BI_0000_Inv_[n]_any_alarm
543 | Available | Binary input | Inv [n] any fault | Boolean | 1 |  | PPC Logic | None | Alarm | Normal | [8 empty] | Change events | KPI | BI_0001_Inv_[n]_any_fault
544 | Available | Binary input | Inv [n] communication failure alarm | Boolean | 2 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | Change events | KPI | BI_0002_Inv_[n]_communication_failure_alarm
545 | Available | Binary input | Inv [n] manual control status | Boolean | 3 |  | PPC Logic | On (1) | Manual | Auto | [8 empty] | Change events | KPI | BI_0003_Inv_[n]_manual_control_status
546 | Available | Binary input | Inv [n] DI01 status | Boolean | 4 |  | IREG_15128.0 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0004_Inv_[n]_DI01_status |  | Need schematic to tell us what function each DI has
547 | Available | Binary input | Inv [n] DI02 status | Boolean | 5 |  | IREG_15128.1 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0005_Inv_[n]_DI02_status |  | Need schematic to tell us what function each DI has
548 | Available | Binary input | Inv [n] DI03 status | Boolean | 6 |  | IREG_15128.2 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0006_Inv_[n]_DI03_status |  | Need schematic to tell us what function each DI has
549 | Available | Binary input | Inv [n] DI04 status | Boolean | 7 |  | IREG_15128.3 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0007_Inv_[n]_DI04_status |  | Need schematic to tell us what function each DI has
550 | Available | Binary input | Inv [n] DI05 status | Boolean | 8 |  | IREG_15128.4 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0008_Inv_[n]_DI05_status |  | Need schematic to tell us what function each DI has
551 | Available | Binary input | Inv [n] DI06 status | Boolean | 9 |  | IREG_15128.5 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0009_Inv_[n]_DI06_status |  | Need schematic to tell us what function each DI has
552 | Available | Binary input | Inv [n] DI07 status | Boolean | 10 |  | IREG_15128.6 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0010_Inv_[n]_DI07_status |  | Need schematic to tell us what function each DI has
553 | Available | Binary input | Inv [n] DI08 status | Boolean | 11 |  | IREG_15128.7 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0011_Inv_[n]_DI08_status |  | Need schematic to tell us what function each DI has
554 | Available | Binary input | Inv [n] DI09 status | Boolean | 12 |  | IREG_15128.8 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0012_Inv_[n]_DI09_status |  | Need schematic to tell us what function each DI has
555 | Available | Binary input | Inv [n] DI10 status | Boolean | 13 |  | IREG_15128.9 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0013_Inv_[n]_DI10_status |  | Need schematic to tell us what function each DI has
556 | Available | Binary input | Inv [n] DI11 status | Boolean | 14 |  | IREG_15128.10 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0014_Inv_[n]_DI11_status |  | Need schematic to tell us what function each DI has
557 | Available | Binary input | Inv [n] DI12 status | Boolean | 15 |  | IREG_15128.11 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0015_Inv_[n]_DI12_status |  | Need schematic to tell us what function each DI has
558 | Available | Binary input | Inv [n] DI13 status | Boolean | 16 |  | IREG_15128.12 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0016_Inv_[n]_DI13_status |  | Need schematic to tell us what function each DI has
559 | Available | Binary input | Inv [n] DI14 status | Boolean | 17 |  | IREG_15128.13 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0017_Inv_[n]_DI14_status |  | Need schematic to tell us what function each DI has
560 | Available | Binary input | Inv [n] DI15 status | Boolean | 18 |  | IREG_15128.14 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0018_Inv_[n]_DI15_status |  | Need schematic to tell us what function each DI has
561 | Available | Binary input | Inv [n] DI16 status | Boolean | 19 |  | IREG_15128.15 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0019_Inv_[n]_DI16_status |  | Need schematic to tell us what function each DI has
562 | Available | Binary input | Inv [n] DI17 status | Boolean | 20 |  | IREG_15128.16 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0020_Inv_[n]_DI17_status |  | Need schematic to tell us what function each DI has
563 | Available | Binary input | Inv [n] DI18 status | Boolean | 21 |  | IREG_15128.17 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0021_Inv_[n]_DI18_status |  | Need schematic to tell us what function each DI has
564 | Available | Binary input | Inv [n] DI19 status | Boolean | 22 |  | IREG_15128.18 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0022_Inv_[n]_DI19_status |  | Need schematic to tell us what function each DI has
565 | Available | Binary input | Inv [n] DI20 status | Boolean | 23 |  | IREG_15128.19 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0023_Inv_[n]_DI20_status |  | Need schematic to tell us what function each DI has
566 | Available | Binary input | Inv [n] DI21 status | Boolean | 24 |  | IREG_15128.20 | None | On | Off | [8 empty] | Change events | Diagnostic | BI_0024_Inv_[n]_DI21_status |  | Need schematic to tell us what function each DI has
567 | Available | Analog output | Inv [n] manual active power setpoint | 32-bit float | 0 |  | PPC Logic |  |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AO_0000_Inv_[n]_manual_active_power_setpoint_kW
568 | Available | Analog output | Inv [n] manual reactive power setpoint | 32-bit float | 1 |  | PPC Logic |  |  |  | kvar or PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AO_0001_Inv_[n]_manual_reactive_power_setpoint_kvar or PU
569 | Available | Analog output | Inv [n] manual reactive power mode | 32-bit signed integer | 2 |  | PPC Logic |  |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Primary Detail | AO_0002_Inv_[n]_manual_reactive_power_mode_enumeration | 0 to 2 | Voltage, Q(U) and Q(P) modes are not selectable through the HMI
570 | Available | Binary output | Inv [n] manual control | Boolean | 0 | LOn:LOff | PPC Logic | None | Manual | Auto | [8 empty] | Change events | Primary Detail | BO_0000_Inv_[n]_manual_control
571 | Available | Binary output | Inv [n] manual start stop | Boolean | 1 | LOn:LOff | PPC Logic | None | Start | Stop | [8 empty] | Change events | Primary Detail | BO_0001_Inv_[n]_manual_start_stop
572 | Available | Binary output | Inv [n] remote emergency stop | Boolean | 2 | LOn:LOff | HREG_15006 | None | E-stop | Normal | [8 empty] | Change events | Primary Detail | BO_0002_Inv_[n]_remote_emergency_stop
573 | Available | Binary output | Inv [n] manual DC switch open close | Boolean | 3 | LOn:LOff | HREG_15059 | None | Close | Open | [8 empty] | Change events | Primary Detail | BO_0003_Inv_[n]_manual_DC_switch_open_close
error
error
error
error
error
error
error
Note on G6: Bit: This field is only defined for binary outputs and for counters used as bitfields. For binary outputs, this is the control bit(s) which are supported, e.g Trip, LatchOn, Pulse etc. Paired bits with opposite meaning are combined with a colon. E.g. Trip:Close or LatchOn:LatchOff. For counters used as bitfields, this field indicates the specific bit of the counter which is represented.
Note on R6: Format: (Low-Low,Low,High,High-High)
Note on W7: Inverter Status: 0 - Not communicating 1 - Fault 2 - Stopped 3 - Running
Note on V13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capitalize first letter after index, capitalize phase identifiers, no _ between phase identifiers
Note on W20: Reactive power mode: 0 - OFF (unregulated unity PF) 1 - Reactive output mode 2 - Power factor mode 3 - Voltage regulation 98 - QU mode 99 - QP mode
Note on W21: Reactive power mode: 0 - OFF (unregulated unity PF) 1 - Reactive output mode 2 - Power factor mode 3 - Voltage regulation 98 - QU mode 99 - QP mode
Note on L22: Josh Walker: If reactive mode is reactive output mode then setpoint is in kvar. If reactive mode is power factor mode then setpoint is power factor in PU
Note on L23: Josh Walker: If reactive mode is reactive output mode then setpoint is in kvar. If reactive mode is power factor mode then setpoint is power factor in PU
Note on W34: Zone Monitor Work State: 0: Disable 1: Self-Study 2: Fault Detection
Note on W45: Inverter Status: 0 - Not communicating 1 - Fault 2 - Stopped 3 - Running
Note on W102: Inverter Status: 0 - Not communicating 1 - Fault 2 - Stopped 3 - Running
Note on W575: Reactive power mode: 0 - OFF (unregulated unity PF) 1 - Reactive output mode 2 - Power factor mode 3 - Voltage regulation 98 - QU mode 99 - QP mode

## PPC to Ignition - SG4400UD
Site Name | [5 empty] | DNP3.0 |  |  | PPC to Ignition - Inverters
Last updated |  | 2023-05-29 | Device Type | PPC |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | Inverters
Replace [n] with PCU number written as 2 digits
List Index | Availability | Object | Point Description | Data Type | DNP index | Bit | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments | Ignt TagPath Prefix: [MidcontinentSolar]Inverters/Inv[n¦00]/ | Offset
1 | Available | Analog input | Inv [n] status | 32-bit float | 0 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0000_Inv_[n]_status_enumeration | 0 to 4 |  | Status/StatusCode (int) Status/Status_string (string)
2 | Available | Analog input | Inv [n] active power | 32-bit float | 1 |  | IREG_15099 | Analog |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,-10,3620,n/a | Out of Band | High resolution | KPI | AI_0001_Inv_[n]_active_power_kW |  |  | Metering/AC/P
3 | Available | Analog input | Inv [n] reactive power | 32-bit float | 2 |  | IREG_15101 | Analog |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,-2180,2180,n/a | Out of Band | High resolution | KPI | AI_0002_Inv_[n]_reactive_power_kvar |  |  | Metering/AC/Q
4 | Available | Analog input | Inv [n] phase A current | 32-bit float | 3 |  | IREG_15096 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0003_Inv_[n]_phase_A_current_A |  |  | Metering/AC/Ia
5 | Available | Analog input | Inv [n] phase B current | 32-bit float | 4 |  | IREG_15097 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0004_Inv_[n]_phase_B_current_A |  |  | Metering/AC/Ib
6 | Available | Analog input | Inv [n] phase C current | 32-bit float | 5 |  | IREG_15098 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0005_Inv_[n]_phase_C_current_A |  |  | Metering/AC/Ic
7 | Available | Analog input | Inv [n] phase AB voltage | 32-bit float | 6 |  | IREG_15093 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0006_Inv_[n]_phase_AB_voltage_V |  |  | Metering/AC/Vab
8 | Available | Analog input | Inv [n] phase BC voltage | 32-bit float | 7 |  | IREG_15094 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0007_Inv_[n]_phase_BC_voltage_V |  |  | Metering/AC/Vbc
9 | Available | Analog input | Inv [n] phase CA voltage | 32-bit float | 8 |  | IREG_15095 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0008_Inv_[n]_phase_CA_voltage_V |  |  | Metering/AC/Vca
10 | Available | Analog input | Inv [n] power factor | 32-bit float | 9 |  | IREG_15105 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0009_Inv_[n]_power_factor_PU |  |  | Metering/AC/PF
11 | Available | Analog input | Inv [n] frequency | 32-bit float | 10 |  | IREG_15106 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0010_Inv_[n]_frequency_Hz |  |  | Metering/AC/f
12 | Available | Analog input | Inv [n] active power setpoint | 32-bit float | 11 |  | PPC Logic | Analog |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,0,3600,n/a | Out of Band | High resolution | KPI | AI_0011_Inv_[n]_active_power_setpoint_kW |  |  | Control/ActivePower/Setpoint
13 | Available | Analog input | Inv [n] active power setpoint feedback | 32-bit float | 12 |  | IREG_15108 | Analog |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | AI_0010 +/- 1% | Not at Setpoint | High resolution | KPI | AI_0012_Inv_[n]_active_power_setpoint_feedback_kW |  |  | Control/ActivePower/SetpointFeedback
14 | Available | Analog input | Inv [n] reactive power mode | 32-bit signed integer | 13 |  | PPC Logic | State change |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Change events | KPI | AI_0013_Inv_[n]_reactive_power_mode_enumeration | 0 to 3, 98,99 | Q(U) and Q(P) modes are not used, but are defined | Control/ReactivePower/ModeCode Control/ReactivePower/Mode_string
15 | Available | Analog input | Inv [n] reactive power mode feedback | 32-bit signed integer | 14 |  | PPC Logic | Analog |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 | AI_0012 +/- 1% | Not at Setpoint | Change events | KPI | AI_0014_Inv_[n]_reactive_power_mode_feedback_enumeration | 0 to 3, 98,99 | Q(U) and Q(P) modes are not used, but are defined | Control/ReactivePower/ModeFeedbackCode Control/ReactivePower/ModeFeedback_string
16 | Available | Analog input | Inv [n] reactive power setpoint | 32-bit float | 15 |  | PPC Logic | Analog |  |  | kvar or PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -2160,-1,1,2160 | 5-State | High resolution | KPI | AI_0015_Inv_[n]_reactive_power_setpoint_kvar or PU |  |  | Control/ReactivePower/Setpoint
17 | Available | Analog input | Inv [n] reactive power setpoint feedback | 32-bit float | 16 |  | IREG_15110 or IREG_15112 | Analog |  |  | kvar or PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | AI_0014 +/- 1% | Not at Setpoint | High resolution | KPI | AI_0016_Inv_[n]_reactive_power_setpoint_feedback_kvar or PU |  |  | Control/ReactivePower/SetpointFeedback
18 | Available | Analog input | Inv [n] total DC power | 32-bit float | 17 |  | IREG_15091 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0017_Inv_[n]_total_DC_power_kW |  |  | Metering/DC/P
19 | Available | Analog input | Inv [n] energy production today | 32-bit float | 18 |  | IREG_15072 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0018_Inv_[n]_energy_production_today_kWh |  |  | Metering/Energy/ProductionToday
20 | Available | Analog input | Inv [n] energy production yesterday | 32-bit float | 19 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0019_Inv_[n]_energy_production_yesterday_kWh |  |  | Metering/Energy/ProductionYesterday
21 | Available | Analog input | Inv [n] total energy production | 32-bit float | 20 |  | IREG_15076 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0020_Inv_[n]_total_energy_production_kWh |  |  | Metering/Energy/ProductionTotal
22 | Available | Analog input | Inv [n] total running hours | 32-bit float | 21 |  | IREG_15081 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0021_Inv_[n]_total_running_hours_hr |  |  | Status/TotalRunningHours
23 | Available | Analog input | Inv [n] transformer oil temperature | 32-bit float | 22 |  | IREG_15118 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -40,-25,50,60 | 5-State | Low resolution | Secondary Detail | AI_0022_Inv_[n]_transformer_oil_temperature_degC |  |  | Transformer/OilTemp
24 | Available | Analog input | Inv [n] transformer winding temperature | 32-bit float | 23 |  | IREG_15119 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | -40,-25,50,60 | 5-State | Low resolution | Secondary Detail | AI_0023_Inv_[n]_transformer_winding_temperature_degC |  |  | Transformer/WindingTemp
25 | Available | Analog input | Inv [n] maximum appearant power | 32-bit float | 24 |  | IREG_15704 | Analog |  |  | kVA | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 | n/a,3600,3600,n/a | Out of Band | Low resolution | Diagnostic | AI_0024_Inv_[n]_maximum_appearant_power_kVA |  | Real time derating | Status/InvRatingLimit/MaximumApparentPower
26 | Available | Analog input | Inv [n] maximum lagging reactive power | 32-bit float | 25 |  | IREG_15706 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0025_Inv_[n]_maximum_lagging_reactive_power_kvar |  |  | Status/InvRatingLimit/MaximumLaggingReactivePower
27 | Available | Analog input | Inv [n] maximum leading reactive power | 32-bit float | 26 |  | IREG_15707 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0026_Inv_[n]_maximum_leading_reactive_power_kvar |  |  | Status/InvRatingLimit/MaximumLeadingReactivePower
28 | Available | Analog input | Inv [n] zone monitor status | 32-bit signed integer | 27 |  | IREG_15999 | None |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Change events | Diagnostic | AI_0027_Inv_[n]_zone_monitor_status_enumeration | 0 to 2 |  | ZoneMonitor/Status/StatusCode (int) ZoneMonitor/Status/Status_string (string)
29 | Available | Analog input | Inv [n] appearant power | 32-bit float | 28 |  | IREG_15104 |  |  |  |  | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Not historized | Not Shown | AI_0028_Inv_[n]_appearant_power |  |  | Spares/SpareAnalog01
30 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 1 | 32-bit signed integer | 29 |  | IREG_16005 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0029_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_1_count |  |  | Spares/SpareAnalog02
31 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 2 | 32-bit signed integer | 30 |  | IREG_16006 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0030_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_2_count |  |  | Spares/SpareAnalog03
32 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 3 | 32-bit signed integer | 31 |  | IREG_16007 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0031_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_3_count |  |  | Spares/SpareAnalog04
33 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 4 | 32-bit signed integer | 32 |  | IREG_16008 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0032_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_4_count |  |  | Spares/SpareAnalog05
34 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 5 | 32-bit signed integer | 33 |  | IREG_16009 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0033_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_5_count |  |  | Spares/SpareAnalog06
35 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 6 | 32-bit signed integer | 34 |  | IREG_16010 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0034_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_6_count |  |  | Spares/SpareAnalog07
36 | Available | Analog input | Inv [n] zone monitor unit 1 warning number of strings branch 7 | 32-bit signed integer | 35 |  | IREG_16011 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0035_Inv_[n]_zone_monitor_unit_1_warning_number_of_strings_branch_7_count |  |  | Spares/SpareAnalog08
37 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 1 | 32-bit signed integer | 36 |  | IREG_16021 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0036_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_1_count |  |  | Spares/SpareAnalog09
38 | Available | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 2 | 32-bit signed integer | 37 |  | IREG_16022 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0037_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_2_count |  |  | Spares/SpareAnalog10
39 |  | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 3 | 32-bit signed integer | 38 |  | IREG_16023 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0038_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_3_count
40 |  | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 4 | 32-bit signed integer | 39 |  | IREG_16024 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0039_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_4_count
41 |  | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 5 | 32-bit signed integer | 40 |  | IREG_16025 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0040_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_5_count
42 |  | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 6 | 32-bit signed integer | 41 |  | IREG_16026 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0041_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_6_count
43 |  | Analog input | Inv [n] zone monitor unit 2 warning number of strings branch 7 | 32-bit signed integer | 42 |  | IREG_16027 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0042_Inv_[n]_zone_monitor_unit_2_warning_number_of_strings_branch_7_count
44 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 1 | 32-bit signed integer | 43 |  | IREG_16037 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0043_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_1_count
45 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 2 | 32-bit signed integer | 44 |  | IREG_16038 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0044_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_2_count
46 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 3 | 32-bit signed integer | 45 |  | IREG_16039 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0045_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_3_count
47 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 4 | 32-bit signed integer | 46 |  | IREG_16040 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0046_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_4_count
48 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 5 | 32-bit signed integer | 47 |  | IREG_16041 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0047_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_5_count
49 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 6 | 32-bit signed integer | 48 |  | IREG_16042 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0048_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_6_count
50 |  | Analog input | Inv [n] zone monitor unit 3 warning number of strings branch 7 | 32-bit signed integer | 49 |  | IREG_16043 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0049_Inv_[n]_zone_monitor_unit_3_warning_number_of_strings_branch_7_count
51 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 1 | 32-bit signed integer | 50 |  | IREG_16053 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0050_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_1_count
52 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 2 | 32-bit signed integer | 51 |  | IREG_16054 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0051_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_2_count
53 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 3 | 32-bit signed integer | 52 |  | IREG_16055 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0052_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_3_count
54 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 4 | 32-bit signed integer | 53 |  | IREG_16056 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0053_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_4_count
55 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 5 | 32-bit signed integer | 54 |  | IREG_16057 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0054_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_5_count
56 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 6 | 32-bit signed integer | 55 |  | IREG_16058 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0055_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_6_count
57 |  | Analog input | Inv [n] zone monitor unit 4 warning number of strings branch 7 | 32-bit signed integer | 56 |  | IREG_16059 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Diagnostic | AI_0056_Inv_[n]_zone_monitor_unit_4_warning_number_of_strings_branch_7_count
58 | Available | Analog input | Inv [n] unit 1 status | 32-bit float | 100 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0100_Inv_[n]_unit_1_status_enumeration | 0 to 4 |  | Module1/Status/StatusCode (int) Module1/Status/Status_string (string) | -19
59 | Available | Analog input | Inv [n] unit 1 active power | 32-bit float | 101 |  | IREG_15169 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0101_Inv_[n]_unit_1_active_power_kW |  |  | Module1/Metering/AC/P | -18
60 | Available | Analog input | Inv [n] unit 1 reactive power | 32-bit float | 102 |  | IREG_15171 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0102_Inv_[n]_unit_1_reactive_power_kvar |  |  | Module1/Metering/AC/Q | -17
61 | Available | Analog input | Inv [n] unit 1 phase A current | 32-bit float | 103 |  | IREG_15166 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0103_Inv_[n]_unit_1_phase_A_current_A |  |  | Module1/Metering/AC/Ia | -16
62 | Available | Analog input | Inv [n] unit 1 phase B current | 32-bit float | 104 |  | IREG_15167 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0104_Inv_[n]_unit_1_phase_B_current_A |  | True if any alarm is set for this inverter | Module1/Metering/AC/Ib | -15
63 | Available | Analog input | Inv [n] unit 1 phase C current | 32-bit float | 105 |  | IREG_15168 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0105_Inv_[n]_unit_1_phase_C_current_A |  |  | Module1/Metering/AC/Ic | -14
64 | Available | Analog input | Inv [n] unit 1 phase AB voltage | 32-bit float | 106 |  | IREG_15163 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0106_Inv_[n]_unit_1_phase_AB_voltage_V |  |  | Module1/Metering/AC/Vab | -13
65 | Available | Analog input | Inv [n] unit 1 phase BC voltage | 32-bit float | 107 |  | IREG_15164 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0107_Inv_[n]_unit_1_phase_BC_voltage_V |  |  | Module1/Metering/AC/Vbc | -12
66 | Available | Analog input | Inv [n] unit 1 phase CA voltage | 32-bit float | 108 |  | IREG_15165 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0108_Inv_[n]_unit_1_phase_CA_voltage_V |  |  | Module1/Metering/AC/Vca | -11
67 | Available | Analog input | Inv [n] unit 1 power factor | 32-bit float | 109 |  | IREG_15173 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0109_Inv_[n]_unit_1_power_factor_PU |  |  | Module1/Metering/AC/PF | -10
68 | Available | Analog input | Inv [n] unit 1 frequency | 32-bit float | 110 |  | IREG_15174 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0110_Inv_[n]_unit_1_frequency_Hz |  |  | Module1/Metering/AC/f | -9
69 | Available | Analog input | Inv [n] unit 1 DC power | 32-bit float | 111 |  | IREG_15161 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0111_Inv_[n]_unit_1_DC_power_kW |  |  | Module1/Metering/DC/P | -8
70 | Available | Analog input | Inv [n] unit 1 total DC current | 32-bit float | 112 |  | IREG_15160 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0112_Inv_[n]_unit_1_total_DC_current_A |  |  | Module1/Metering/DC/I | -7
71 | Available | Analog input | Inv [n] unit 1 DC voltage | 32-bit float | 113 |  | IREG_15159 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0113_Inv_[n]_unit_1_DC_voltage_V |  |  | Module1/Metering/DC/V | -6
72 | Available | Analog input | Inv [n] unit 1 DC Input 1 | 32-bit float | 114 |  | IREG_15029 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0114_Inv_[n]_unit_1_DC_Input_1_A |  |  | Module1/Branches/01/Current
73 | Available | Analog input | Inv [n] unit 1 DC Input 2 | 32-bit float | 115 |  | IREG_15030 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0115_Inv_[n]_unit_1_DC_Input_2_A |  |  | Module1/Branches/02/Current
74 | Available | Analog input | Inv [n] unit 1 DC Input 3 | 32-bit float | 116 |  | IREG_15031 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0116_Inv_[n]_unit_1_DC_Input_3_A |  |  | Module1/Branches/03/Current
75 | Available | Analog input | Inv [n] unit 1 DC Input 4 | 32-bit float | 117 |  | IREG_15032 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0117_Inv_[n]_unit_1_DC_Input_4_A |  |  | Module1/Branches/04/Current
76 | Available | Analog input | Inv [n] unit 1 DC Input 5 | 32-bit float | 118 |  | IREG_15033 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0118_Inv_[n]_unit_1_DC_Input_5_A |  |  | Module1/Branches/05/Current
77 | Available | Analog input | Inv [n] unit 1 DC Input 6 | 32-bit float | 119 |  | IREG_15034 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0119_Inv_[n]_unit_1_DC_Input_6_A |  |  | Module1/Branches/06/Current
78 | Available | Analog input | Inv [n] unit 1 DC Input 7 | 32-bit float | 120 |  | IREG_15035 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0120_Inv_[n]_unit_1_DC_Input_7_A |  |  | Module1/Branches/07/Current
79 | Available | Analog input | Inv [n] unit 1 energy production today | 32-bit float | 134 |  | IREG_15149 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0134_Inv_[n]_unit_1_energy_production_today_kWh |  |  | Module1/Metering/Energy/ProductionToday | -5
80 | Available | Analog input | Inv [n] unit 1 energy production yesterday | 32-bit float | 135 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0135_Inv_[n]_unit_1_energy_production_yesterday_kWh |  |  | Module1/Metering/Energy/ProductionYesterday | -4
81 | Available | Analog input | Inv [n] unit 1 total energy production | 32-bit float | 136 |  | IREG_15153 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0136_Inv_[n]_unit_1_total_energy_production_kWh |  |  | Module1/Metering/Energy/ProductionTotal | -3
82 | Available | Analog input | Inv [n] unit 1 total running hours | 32-bit float | 137 |  | IREG_15156 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0137_Inv_[n]_unit_1_total_running_hours_hr |  |  | Module1/Status/TotalRunningHours | -2
83 | Available | Analog input | Inv [n] unit 1 internal module temperature | 32-bit float | 138 |  | IREG_15158 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  | 5-State | Low resolution | Diagnostic | AI_0138_Inv_[n]_unit_1_internal_module_temperature_degC |  |  | Module1/Temperature/InternalModuleTemp | -1
84 |  | Analog input | Inv [n] unit 1 daily grid connected minutes | 32-bit float | 139 |  | IREG_15156 | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0139_Inv_[n]_unit_1_daily_grid_connected_minutes_min
85 | Available | Analog input | Inv [n] unit 1 yesterday grid connected minutes | 32-bit float | 140 |  | PPC Logic | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0140_Inv_[n]_unit_1_yesterday_grid_connected_minutes_min |  |  | Module1/YesterdayGridConnectedMinutes | 0
86 | Available | Analog input | Inv [n] unit 1 efficiency | 32-bit float | 141 |  | IREG_15175 | None |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0141_Inv_[n]_unit_1_efficiency_pct |  |  | Module1/Efficiency | 1
87 | Available | Analog input | Inv [n] unit 1 positive resitance to ground | 32-bit float | 142 |  | IREG_15203 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0142_Inv_[n]_unit_1_positive_resitance_to_ground_kOhm |  |  | Module1/Metering/Ground/RpositiveToGround | 2
88 | Available | Analog input | Inv [n] unit 1 negative resitance to ground | 32-bit float | 143 |  | IREG_15205 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0143_Inv_[n]_unit_1_negative_resitance_to_ground_kOhm |  |  | Module1/Metering/Ground/RnegativeToGround | 3
89 | Available | Analog input | Inv [n] unit 1 negative voltage to ground | 32-bit float | 144 |  | IREG_15211 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0144_Inv_[n]_unit_1_negative_voltage_to_ground_V |  |  | Module1/Metering/Ground/VnegativeToGround | 4
90 | Available | Analog input | Inv [n] unit 1 leakage current | 32-bit float | 145 |  | IREG_15733 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0145_Inv_[n]_unit_1_leakage_current_count |  |  | Module1/Status/EventRecorderRecordCount | 21
91 | Available | Analog input | Inv [n] unit 1 temperature 1 | 32-bit float | 146 |  | IREG_15198 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0146_Inv_[n]_unit_1_temperature_1_degC |  |  | Module1/Temperature/ACcabinetTemp | 22
92 | Available | Analog input | Inv [n] unit 1 temperature 3 | 32-bit float | 147 |  | IREG_15200 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0147_Inv_[n]_unit_1_temperature_3_degC |  |  | Module1/Temperature/DCcabinetTemp | 23
93 | Available | Analog input | Inv [n] unit 1 temperature 5 | 32-bit float | 148 |  | IREG_15202 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0148_Inv_[n]_unit_1_temperature_5_degC |  |  | Module1/Temperature/ControlCabinetTemp | 24
94 |  | Analog input | Inv [n] unit 1 event recorder count | 32-bit float | 149 |  | IREG_15733 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0149_Inv_[n]_unit_1_event_recorder_count_count
95 |  | Analog input | Inv [n] unit 2 status | 32-bit float | 200 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail
96 |  | Analog input | Inv [n] unit 2 active power | 32-bit float | 201 |  | IREG_15169 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
97 |  | Analog input | Inv [n] unit 2 reactive power | 32-bit float | 202 |  | IREG_15171 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
98 |  | Analog input | Inv [n] unit 2 phase A current | 32-bit float | 203 |  | IREG_15166 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
99 |  | Analog input | Inv [n] unit 2 phase B current | 32-bit float | 204 |  | IREG_15167 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
100 |  | Analog input | Inv [n] unit 2 phase C current | 32-bit float | 205 |  | IREG_15168 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
101 |  | Analog input | Inv [n] unit 2 phase AB voltage | 32-bit float | 206 |  | IREG_15163 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
102 |  | Analog input | Inv [n] unit 2 phase BC voltage | 32-bit float | 207 |  | IREG_15164 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
103 |  | Analog input | Inv [n] unit 2 phase CA voltage | 32-bit float | 208 |  | IREG_15165 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
104 |  | Analog input | Inv [n] unit 2 power factor | 32-bit float | 209 |  | IREG_15173 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
105 |  | Analog input | Inv [n] unit 2 frequency | 32-bit float | 210 |  | IREG_15174 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
106 |  | Analog input | Inv [n] unit 2 DC power | 32-bit float | 211 |  | IREG_15161 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
107 |  | Analog input | Inv [n] unit 2 total DC current | 32-bit float | 212 |  | IREG_15160 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
108 |  | Analog input | Inv [n] unit 2 DC voltage | 32-bit float | 213 |  | IREG_15159 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail
109 |  | Analog input | Inv [n] unit 2 DC Input 1 | 32-bit float | 214 |  | IREG_15029 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
110 |  | Analog input | Inv [n] unit 2 DC Input 2 | 32-bit float | 215 |  | IREG_15030 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
111 |  | Analog input | Inv [n] unit 2 DC Input 3 | 32-bit float | 216 |  | IREG_15031 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
112 |  | Analog input | Inv [n] unit 2 DC Input 4 | 32-bit float | 217 |  | IREG_15032 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
113 |  | Analog input | Inv [n] unit 2 DC Input 5 | 32-bit float | 218 |  | IREG_15033 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
114 |  | Analog input | Inv [n] unit 2 DC Input 6 | 32-bit float | 219 |  | IREG_15034 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
115 |  | Analog input | Inv [n] unit 2 DC Input 7 | 32-bit float | 220 |  | IREG_15035 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic
116 |  | Analog input | Inv [n] unit 2 energy production today | 32-bit float | 234 |  | IREG_15149 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail
117 |  | Analog input | Inv [n] unit 2 energy production yesterday | 32-bit float | 235 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail
118 |  | Analog input | Inv [n] unit 2 total energy production | 32-bit float | 236 |  | IREG_15153 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
119 |  | Analog input | Inv [n] unit 2 total running hours | 32-bit float | 237 |  | IREG_15156 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
120 |  | Analog input | Inv [n] unit 2 internal module temperature | 32-bit float | 238 |  | IREG_15158 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  | 5-State | Low resolution | Diagnostic
121 |  | Analog input | Inv [n] unit 2 daily grid connected minutes | 32-bit float | 239 |  | IREG_15156 | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic
122 |  | Analog input | Inv [n] unit 2 yesterday grid connected minutes | 32-bit float | 240 |  | PPC Logic | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic
123 |  | Analog input | Inv [n] unit 2 efficiency | 32-bit float | 241 |  | IREG_15175 | None |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail
124 |  | Analog input | Inv [n] unit 2 positive resitance to ground | 32-bit float | 242 |  | IREG_15203 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
125 |  | Analog input | Inv [n] unit 2 negative resitance to ground | 32-bit float | 243 |  | IREG_15205 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
126 |  | Analog input | Inv [n] unit 2 negative voltage to ground | 32-bit float | 244 |  | IREG_15211 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
127 |  | Analog input | Inv [n] unit 2 leakage current | 32-bit float | 245 |  | IREG_15733 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic
128 |  | Analog input | Inv [n] unit 2 temperature 1 | 32-bit float | 246 |  | IREG_15198 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
129 |  | Analog input | Inv [n] unit 2 temperature 3 | 32-bit float | 247 |  | IREG_15200 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
130 |  | Analog input | Inv [n] unit 2 temperature 5 | 32-bit float | 248 |  | IREG_15202 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
131 |  | Analog input | Inv [n] unit 2 event recorder count | 32-bit float | 149 |  | IREG_15734 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0149_Inv_[n]_unit_2_event_recorder_count_count
132 |  | Analog input | Inv [n] unit 3 status | 32-bit float | 300 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail
133 |  | Analog input | Inv [n] unit 3 active power | 32-bit float | 301 |  | IREG_15169 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0301_Inv_[n]_unit_3_active_power_kW
134 |  | Analog input | Inv [n] unit 3 reactive power | 32-bit float | 302 |  | IREG_15171 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0302_Inv_[n]_unit_3_reactive_power_kvar
135 |  | Analog input | Inv [n] unit 3 phase A current | 32-bit float | 303 |  | IREG_15166 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0303_Inv_[n]_unit_3_phase_A_current_A
136 |  | Analog input | Inv [n] unit 3 phase B current | 32-bit float | 304 |  | IREG_15167 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0304_Inv_[n]_unit_3_phase_B_current_A
137 |  | Analog input | Inv [n] unit 3 phase C current | 32-bit float | 305 |  | IREG_15168 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0305_Inv_[n]_unit_3_phase_C_current_A
138 |  | Analog input | Inv [n] unit 3 phase AB voltage | 32-bit float | 306 |  | IREG_15163 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0306_Inv_[n]_unit_3_phase_AB_voltage_V
139 |  | Analog input | Inv [n] unit 3 phase BC voltage | 32-bit float | 307 |  | IREG_15164 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0307_Inv_[n]_unit_3_phase_BC_voltage_V
140 |  | Analog input | Inv [n] unit 3 phase CA voltage | 32-bit float | 308 |  | IREG_15165 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0308_Inv_[n]_unit_3_phase_CA_voltage_V
141 |  | Analog input | Inv [n] unit 3 power factor | 32-bit float | 309 |  | IREG_15173 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0309_Inv_[n]_unit_3_power_factor_PU
142 |  | Analog input | Inv [n] unit 3 frequency | 32-bit float | 310 |  | IREG_15174 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0310_Inv_[n]_unit_3_frequency_Hz
143 |  | Analog input | Inv [n] unit 3 DC power | 32-bit float | 311 |  | IREG_15161 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0311_Inv_[n]_unit_3_DC_power_kW
144 |  | Analog input | Inv [n] unit 3 total DC current | 32-bit float | 312 |  | IREG_15160 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0312_Inv_[n]_unit_3_total_DC_current_A
145 |  | Analog input | Inv [n] unit 3 DC voltage | 32-bit float | 313 |  | IREG_15159 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0313_Inv_[n]_unit_3_DC_voltage_V
146 |  | Analog input | Inv [n] unit 3 DC Input 1 | 32-bit float | 314 |  | IREG_15029 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0314_Inv_[n]_unit_3_DC_Input_1_A
147 |  | Analog input | Inv [n] unit 3 DC Input 2 | 32-bit float | 315 |  | IREG_15030 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0315_Inv_[n]_unit_3_DC_Input_2_A
148 |  | Analog input | Inv [n] unit 3 DC Input 3 | 32-bit float | 316 |  | IREG_15031 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0316_Inv_[n]_unit_3_DC_Input_3_A
149 |  | Analog input | Inv [n] unit 3 DC Input 4 | 32-bit float | 317 |  | IREG_15032 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0317_Inv_[n]_unit_3_DC_Input_4_A
150 |  | Analog input | Inv [n] unit 3 DC Input 5 | 32-bit float | 318 |  | IREG_15033 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0318_Inv_[n]_unit_3_DC_Input_5_A
151 |  | Analog input | Inv [n] unit 3 DC Input 6 | 32-bit float | 319 |  | IREG_15034 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0319_Inv_[n]_unit_3_DC_Input_6_A
152 |  | Analog input | Inv [n] unit 3 DC Input 7 | 32-bit float | 320 |  | IREG_15035 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0320_Inv_[n]_unit_3_DC_Input_7_A
153 |  | Analog input | Inv [n] unit 3 energy production today | 32-bit float | 334 |  | IREG_15149 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0334_Inv_[n]_unit_3_energy_production_today_kWh
154 |  | Analog input | Inv [n] unit 3 energy production yesterday | 32-bit float | 335 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0335_Inv_[n]_unit_3_energy_production_yesterday_kWh
155 |  | Analog input | Inv [n] unit 3 total energy production | 32-bit float | 336 |  | IREG_15153 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0336_Inv_[n]_unit_3_total_energy_production_kWh
156 |  | Analog input | Inv [n] unit 3 total running hours | 32-bit float | 337 |  | IREG_15156 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0337_Inv_[n]_unit_3_total_running_hours_hr
157 |  | Analog input | Inv [n] unit 3 internal module temperature | 32-bit float | 338 |  | IREG_15158 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  | 5-State | Low resolution | Diagnostic | AI_0338_Inv_[n]_unit_3_internal_module_temperature_degC
158 |  | Analog input | Inv [n] unit 3 daily grid connected minutes | 32-bit float | 339 |  | IREG_15156 | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0339_Inv_[n]_unit_3_daily_grid_connected_minutes_min
159 |  | Analog input | Inv [n] unit 3 yesterday grid connected minutes | 32-bit float | 340 |  | PPC Logic | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0340_Inv_[n]_unit_3_yesterday_grid_connected_minutes_min
160 |  | Analog input | Inv [n] unit 3 efficiency | 32-bit float | 341 |  | IREG_15175 | None |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0341_Inv_[n]_unit_3_efficiency_pct
161 |  | Analog input | Inv [n] unit 3 positive resitance to ground | 32-bit float | 342 |  | IREG_15203 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0342_Inv_[n]_unit_3_positive_resitance_to_ground_kOhm
162 |  | Analog input | Inv [n] unit 3 negative resitance to ground | 32-bit float | 343 |  | IREG_15205 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0343_Inv_[n]_unit_3_negative_resitance_to_ground_kOhm
163 |  | Analog input | Inv [n] unit 3 negative voltage to ground | 32-bit float | 344 |  | IREG_15211 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0344_Inv_[n]_unit_3_negative_voltage_to_ground_V
164 |  | Analog input | Inv [n] unit 3 leakage current | 32-bit float | 345 |  | IREG_15733 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0345_Inv_[n]_unit_3_leakage_current_count
165 |  | Analog input | Inv [n] unit 3 temperature 1 | 32-bit float | 346 |  | IREG_15198 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0346_Inv_[n]_unit_3_temperature_1_degC
166 |  | Analog input | Inv [n] unit 3 temperature 3 | 32-bit float | 347 |  | IREG_15200 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0347_Inv_[n]_unit_3_temperature_3_degC
167 |  | Analog input | Inv [n] unit 3 temperature 5 | 32-bit float | 348 |  | IREG_15202 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic | AI_0348_Inv_[n]_unit_3_temperature_5_degC
168 |  | Analog input | Inv [n] unit 3 event recorder count | 32-bit float | 149 |  | IREG_15735 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0149_Inv_[n]_unit_3_event_recorder_count_count
169 |  | Analog input | Inv [n] unit 4 status | 32-bit float | 400 |  | PPC Logic | None |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail | AI_0400_Inv_[n]_unit_4_status_enumeration
170 |  | Analog input | Inv [n] unit 4 active power | 32-bit float | 401 |  | IREG_15169 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0401_Inv_[n]_unit_4_active_power_kW
171 |  | Analog input | Inv [n] unit 4 reactive power | 32-bit float | 402 |  | IREG_15171 | None |  |  | kvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0402_Inv_[n]_unit_4_reactive_power_kvar
172 |  | Analog input | Inv [n] unit 4 phase A current | 32-bit float | 403 |  | IREG_15166 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0403_Inv_[n]_unit_4_phase_A_current_A
173 |  | Analog input | Inv [n] unit 4 phase B current | 32-bit float | 404 |  | IREG_15167 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0404_Inv_[n]_unit_4_phase_B_current_A
174 |  | Analog input | Inv [n] unit 4 phase C current | 32-bit float | 405 |  | IREG_15168 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0405_Inv_[n]_unit_4_phase_C_current_A
175 |  | Analog input | Inv [n] unit 4 phase AB voltage | 32-bit float | 406 |  | IREG_15163 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0406_Inv_[n]_unit_4_phase_AB_voltage_V
176 |  | Analog input | Inv [n] unit 4 phase BC voltage | 32-bit float | 407 |  | IREG_15164 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0407_Inv_[n]_unit_4_phase_BC_voltage_V
177 |  | Analog input | Inv [n] unit 4 phase CA voltage | 32-bit float | 408 |  | IREG_15165 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0408_Inv_[n]_unit_4_phase_CA_voltage_V
178 |  | Analog input | Inv [n] unit 4 power factor | 32-bit float | 409 |  | IREG_15173 | None |  |  | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0409_Inv_[n]_unit_4_power_factor_PU
179 |  | Analog input | Inv [n] unit 4 frequency | 32-bit float | 410 |  | IREG_15174 | None |  |  | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0410_Inv_[n]_unit_4_frequency_Hz
180 |  | Analog input | Inv [n] unit 4 DC power | 32-bit float | 411 |  | IREG_15161 | None |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0411_Inv_[n]_unit_4_DC_power_kW
181 |  | Analog input | Inv [n] unit 4 total DC current | 32-bit float | 412 |  | IREG_15160 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0412_Inv_[n]_unit_4_total_DC_current_A
182 |  | Analog input | Inv [n] unit 4 DC voltage | 32-bit float | 413 |  | IREG_15159 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0413_Inv_[n]_unit_4_DC_voltage_V
183 |  | Analog input | Inv [n] unit 4 DC Input 1 | 32-bit float | 414 |  | IREG_15029 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0414_Inv_[n]_unit_4_DC_Input_1_A
184 |  | Analog input | Inv [n] unit 4 DC Input 2 | 32-bit float | 415 |  | IREG_15030 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0415_Inv_[n]_unit_4_DC_Input_2_A
185 |  | Analog input | Inv [n] unit 4 DC Input 3 | 32-bit float | 416 |  | IREG_15031 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0416_Inv_[n]_unit_4_DC_Input_3_A
186 |  | Analog input | Inv [n] unit 4 DC Input 4 | 32-bit float | 417 |  | IREG_15032 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0417_Inv_[n]_unit_4_DC_Input_4_A
187 |  | Analog input | Inv [n] unit 4 DC Input 5 | 32-bit float | 418 |  | IREG_15033 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0418_Inv_[n]_unit_4_DC_Input_5_A
188 |  | Analog input | Inv [n] unit 4 DC Input 6 | 32-bit float | 419 |  | IREG_15034 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0419_Inv_[n]_unit_4_DC_Input_6_A
189 |  | Analog input | Inv [n] unit 4 DC Input 7 | 32-bit float | 420 |  | IREG_15035 | None |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Analytic | AI_0420_Inv_[n]_unit_4_DC_Input_7_A
190 |  | Analog input | Inv [n] unit 4 energy production today | 32-bit float | 434 |  | IREG_15149 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AI_0434_Inv_[n]_unit_4_energy_production_today_kWh
191 |  | Analog input | Inv [n] unit 4 energy production yesterday | 32-bit float | 435 |  | PPC Logic | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Primary Detail
192 |  | Analog input | Inv [n] unit 4 total energy production | 32-bit float | 436 |  | IREG_15153 | None |  |  | kWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
193 |  | Analog input | Inv [n] unit 4 total running hours | 32-bit float | 437 |  | IREG_15156 | None |  |  | hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
194 |  | Analog input | Inv [n] unit 4 internal module temperature | 32-bit float | 438 |  | IREG_15158 | Analog |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  | 5-State | Low resolution | Diagnostic
195 |  | Analog input | Inv [n] unit 4 daily grid connected minutes | 32-bit float | 439 |  | IREG_15156 | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic
196 |  | Analog input | Inv [n] unit 4 yesterday grid connected minutes | 32-bit float | 440 |  | PPC Logic | None |  |  | min | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic
197 |  | Analog input | Inv [n] unit 4 efficiency | 32-bit float | 441 |  | IREG_15175 | None |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail
198 |  | Analog input | Inv [n] unit 4 positive resitance to ground | 32-bit float | 442 |  | IREG_15203 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
199 |  | Analog input | Inv [n] unit 4 negative resitance to ground | 32-bit float | 443 |  | IREG_15205 | None |  |  | kOhm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
200 |  | Analog input | Inv [n] unit 4 negative voltage to ground | 32-bit float | 444 |  | IREG_15211 | None |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
201 |  | Analog input | Inv [n] unit 4 leakage current | 32-bit float | 445 |  | IREG_15733 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic
202 |  | Analog input | Inv [n] unit 4 temperature 1 | 32-bit float | 446 |  | IREG_15198 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
203 |  | Analog input | Inv [n] unit 4 temperature 3 | 32-bit float | 447 |  | IREG_15200 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
204 |  | Analog input | Inv [n] unit 4 temperature 5 | 32-bit float | 448 |  | IREG_15202 | None |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Diagnostic
205 |  | Analog input | Inv [n] unit 4 event recorder count | 32-bit float | 149 |  | IREG_15736 | None |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | Diagnostic | AI_0149_Inv_[n]_unit_4_event_recorder_count_count
206 | Available | Counter | Inv [n] skid level status register | 32-bit bitfield | 0 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0000_Inv_[n]_skid_level_status_register
207 | Available | Counter | Inv [n] MV load switch status | 32-bit bitfield | 0 | 0 | IREG_15131.0 | None | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_MV_load_switch_status
208 | Available | Counter | Inv [n] HV remote control | 32-bit bitfield | 0 | 1 | IREG_15126.14 | None | Local | Remote | [8 empty] | Change events |  | CNT_0000_Inv_[n]_HV_remote_control
209 | Available | Counter | Inv [n] Inverter is Running | 32-bit bitfield | 0 | 2 | IREG_15117.0 | None | Running | Stopped | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Inverter_is_Running
210 |  | Counter | Inv [n] Inverter is Stopped | 32-bit bitfield | 0 | 3 | IREG_15117.1 | None | Stopped | Running | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Inverter_is_Stopped
211 | Available | Counter | Inv [n] Remote E-stop | 32-bit bitfield | 0 | 4 | IREG_15117.3 | On (1) | Alarm | Normal | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Remote_E_stop
212 | Available | Counter | Inv [n] Local E-stop | 32-bit bitfield | 0 | 5 | IREG_15117.6 | On (1) | Alarm | Normal | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Local_E_stop
213 | Available | Counter | Inv [n] Running | 32-bit bitfield | 0 | 6 | IREG_15117.8 | None | On | Off | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Running
214 |  | Counter | Inv [n] Warn Run | 32-bit bitfield | 0 | 7 | IREG_15117.9 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Warn_Run
215 |  | Counter | Inv [n] Fault | 32-bit bitfield | 0 | 8 | IREG_15117.10 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Fault
216 |  | Counter | Inv [n] Stop | 32-bit bitfield | 0 | 9 | IREG_15117.11 | None | On | Off | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Stop
217 |  | Counter | Inv [n] HV room door | 32-bit bitfield | 0 | 10 | IREG_15126.6 | On (1) | Open | Closed | [8 empty] | Change events |  | CNT_0000_Inv_[n]_HV_room_door
218 |  | Counter | Inv [n] External E-stop | 32-bit bitfield | 0 | 11 | IREG_15126.11 | On (1) | Alarm | Normal | [8 empty] | Change events |  | CNT_0000_Inv_[n]_External_E_stop
219 |  | Counter | Inv [n] HV remote control trip | 32-bit bitfield | 0 | 12 | IREG_15131.1 | None | Active | Normal | [8 empty] | Change events |  | CNT_0000_Inv_[n]_HV_remote_control_trip
220 |  | Counter | Inv [n] HV remote control close | 32-bit bitfield | 0 | 13 | IREG_15131.6 | None | Active | Normal | [8 empty] | Change events |  | CNT_0000_Inv_[n]_HV_remote_control_close
221 |  | Counter | Inv [n] Transformer room door | 32-bit bitfield | 0 | 14 | IREG_15131.7 | On (1) | Open | Closed | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Transformer_room_door
222 |  | Counter | Inv [n] MV earthing switch | 32-bit bitfield | 0 | 15 | IREG_15131.11 | On (1) | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_MV_earthing_switch
223 |  | Counter | Inv [n] MV earthing switch 1 | 32-bit bitfield | 0 | 16 | IREG_15131.12 | On (1) | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_MV_earthing_switch_1
224 |  | Counter | Inv [n] MV earthing switch 2 | 32-bit bitfield | 0 | 17 | IREG_15131.13 | On (1) | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_MV_earthing_switch_2
225 |  | Counter | Inv [n] MV earthing switch 3 | 32-bit bitfield | 0 | 18 | IREG_15131.14 | On (1) | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_MV_earthing_switch_3
226 |  | Counter | Inv [n] Load switch T-A status | 32-bit bitfield | 0 | 19 | IREG_15131.18 | None | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Load_switch_T_A_status
227 |  | Counter | Inv [n] Load switch T-B status | 32-bit bitfield | 0 | 20 | IREG_15131.19 | None | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Load_switch_T_B_status
228 |  | Counter | Inv [n] Load switch T-AB status | 32-bit bitfield | 0 | 21 | IREG_15131.20 | None | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Load_switch_T_AB_status
229 |  | Counter | Inv [n] Load switch A-B status | 32-bit bitfield | 0 | 22 | IREG_15131.21 | None | Closed | Open | [8 empty] | Change events |  | CNT_0000_Inv_[n]_Load_switch_A_B_status
230 |  | Counter | Inv [n] Skid level faults register | 32-bit bitfield | 1 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0001_Inv_[n]_Skid_level_faults_register
231 |  | Counter | Inv [n] SCU master fault | 32-bit bitfield | 1 | 0 | IREG_15117.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_SCU_master_fault
232 |  | Counter | Inv [n] AC insulation fault | 32-bit bitfield | 1 | 1 | IREG_15117.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_AC_insulation_fault
233 |  | Counter | Inv [n] SCU slave fault | 32-bit bitfield | 1 | 2 | IREG_15117.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_SCU_slave_fault
234 |  | Counter | Inv [n] 24hr insulation fault | 32-bit bitfield | 1 | 3 | IREG_15117.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_24hr_insulation_fault
235 |  | Counter | Inv [n] 24hr DC insulation fault | 32-bit bitfield | 1 | 4 | IREG_15117.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_24hr_DC_insulation_fault
236 |  | Counter | Inv [n] 24hr AC insulation fault | 32-bit bitfield | 1 | 5 | IREG_15117.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_24hr_AC_insulation_fault
237 |  | Counter | Inv [n] ISO insulation detection abnormal fault | 32-bit bitfield | 1 | 6 | IREG_15630.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_ISO_insulation_detection_abnormal_fault
238 |  | Counter | Inv [n] ISO hardware fault | 32-bit bitfield | 1 | 7 | IREG_15630.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_ISO_hardware_fault
239 |  | Counter | Inv [n] ISO overtemperature fault | 32-bit bitfield | 1 | 8 | IREG_15630.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_ISO_overtemperature_fault
240 |  | Counter | Inv [n] ISO overvoltage fault | 32-bit bitfield | 1 | 9 | IREG_15630.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0001_Inv_[n]_ISO_overvoltage_fault
241 |  | Counter | Inv [n] Skid level alarms register | 32-bit bitfield | 2 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_Skid_level_alarms_register
242 |  | Counter | Inv [n] ISO insulation detection abnormal alarm | 32-bit bitfield | 2 | 0 | IREG_15631.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_ISO_insulation_detection_abnormal_alarm
243 |  | Counter | Inv [n] ISO overtemperature alarm | 32-bit bitfield | 2 | 1 | IREG_15631.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_ISO_overtemperature_alarm
244 |  | Counter | Inv [n] ISO grid sampling abnormal alarm | 32-bit bitfield | 2 | 2 | IREG_15631.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_ISO_grid_sampling_abnormal_alarm
245 |  | Counter | Inv [n] MV fuse | 32-bit bitfield | 2 | 3 | IREG_15126.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_MV_fuse
246 |  | Counter | Inv [n] HV room smoke | 32-bit bitfield | 2 | 4 | IREG_15126.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_HV_room_smoke
247 |  | Counter | Inv [n] Transformer room smoke | 32-bit bitfield | 2 | 5 | IREG_15131.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_Transformer_room_smoke
248 |  | Counter | Inv [n] UPS alarm | 32-bit bitfield | 2 | 6 | IREG_15131.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_UPS_alarm
249 |  | Counter | Inv [n] High level trip | 32-bit bitfield | 2 | 7 | IREG_15131.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_High_level_trip
250 |  | Counter | Inv [n] MV fan alarm | 32-bit bitfield | 2 | 8 | IREG_15127.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_MV_fan_alarm
251 |  | Counter | Inv [n] AC insulation detection comm failure | 32-bit bitfield | 2 | 9 | IREG_15127.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_AC_insulation_detection_comm_failure
252 |  | Counter | Inv [n] 24hr insulation alarm | 32-bit bitfield | 2 | 10 | IREG_15127.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_24hr_insulation_alarm
253 |  | Counter | Inv [n] SCU master-slave comm failure | 32-bit bitfield | 2 | 11 | IREG_15127.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_SCU_master_slave_comm_failure
254 |  | Counter | Inv [n] Heartbeat abnormal | 32-bit bitfield | 2 | 12 | IREG_15127.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_Heartbeat_abnormal
255 |  | Counter | Inv [n] PMD IO board comm failure | 32-bit bitfield | 2 | 13 | IREG_15127.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_PMD_IO_board_comm_failure
256 |  | Counter | Inv [n] Inverter IO board comm failure | 32-bit bitfield | 2 | 14 | IREG_15127.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_Inverter_IO_board_comm_failure
257 |  | Counter | Inv [n] ISO board comm failure | 32-bit bitfield | 2 | 15 | IREG_15127.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_ISO_board_comm_failure
258 |  | Counter | Inv [n] UPS fault alarm | 32-bit bitfield | 2 | 16 | IREG_15147.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_UPS_fault_alarm
259 |  | Counter | Inv [n] UPS bypass alarm | 32-bit bitfield | 2 | 17 | IREG_15147.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_UPS_bypass_alarm
260 |  | Counter | Inv [n] UPS battery undervoltage alarm | 32-bit bitfield | 2 | 18 | IREG_15147.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_UPS_battery_undervoltage_alarm
261 |  | Counter | Inv [n] UPS mains disconnection alarm | 32-bit bitfield | 2 | 19 | IREG_15147.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_UPS_mains_disconnection_alarm |  | Need schematic to tell us what function each DI has
262 |  | Counter | Inv [n] UPS conversion | 32-bit bitfield | 2 | 20 | IREG_15146.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0002_Inv_[n]_UPS_conversion |  | Need schematic to tell us what function each DI has
263 |  | Counter | Inv [n] Skid transformer alarms register | 32-bit bitfield | 3 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0003_Inv_[n]_Skid_transformer_alarms_register
264 |  | Counter | Inv [n] Gas relay trip | 32-bit bitfield | 3 | 3 | IREG_15114.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Gas_relay_trip |  | Need schematic to tell us what function each DI has
265 |  | Counter | Inv [n] Gas relay alarm | 32-bit bitfield | 3 | 4 | IREG_15114.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Gas_relay_alarm |  | Need schematic to tell us what function each DI has
266 |  | Counter | Inv [n] Oil temperature alarm | 32-bit bitfield | 3 | 5 | IREG_15114.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Oil_temperature_alarm |  | Need schematic to tell us what function each DI has
267 |  | Counter | Inv [n] Oil temperature trip | 32-bit bitfield | 3 | 6 | IREG_15114.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Oil_temperature_trip |  | Need schematic to tell us what function each DI has
268 |  | Counter | Inv [n] Low oil level trip | 32-bit bitfield | 3 | 7 | IREG_15114.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Low_oil_level_trip |  | Need schematic to tell us what function each DI has
269 |  | Counter | Inv [n] Low oil level alarm | 32-bit bitfield | 3 | 8 | IREG_15114.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Low_oil_level_alarm |  | Need schematic to tell us what function each DI has
270 |  | Counter | Inv [n] Pressure relief trip | 32-bit bitfield | 3 | 9 | IREG_15114.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Pressure_relief_trip |  | Need schematic to tell us what function each DI has
271 |  | Counter | Inv [n] MV load switch 1 | 32-bit bitfield | 3 | 10 | IREG_15114.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_MV_load_switch_1 |  | Need schematic to tell us what function each DI has
272 |  | Counter | Inv [n] MV load switch 2 status | 32-bit bitfield | 3 | 11 | IREG_15114.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_MV_load_switch_2_status |  | Need schematic to tell us what function each DI has
273 |  | Counter | Inv [n] MV disconnector switch status | 32-bit bitfield | 3 | 12 | IREG_15114.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_MV_disconnector_switch_status |  | Need schematic to tell us what function each DI has
274 |  | Counter | Inv [n] High level alarm | 32-bit bitfield | 3 | 13 | IREG_15114.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_High_level_alarm |  | Need schematic to tell us what function each DI has
275 |  | Counter | Inv [n] Winding temperature trip | 32-bit bitfield | 3 | 14 | IREG_15114.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Winding_temperature_trip |  | Need schematic to tell us what function each DI has
276 |  | Counter | Inv [n] Winding temperature alarm | 32-bit bitfield | 3 | 15 | IREG_15114.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0003_Inv_[n]_Winding_temperature_alarm |  | Need schematic to tell us what function each DI has
277 |  | Counter | Inv [n] Skid digital inputs register | 32-bit bitfield | 4 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0004_Inv_[n]_Skid_digital_inputs_register
278 |  | Counter | Inv [n] DI01 status | 32-bit bitfield | 4 | 0 | IREG_15129.0 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI01_status |  | Need schematic to tell us what function each DI has
279 |  | Counter | Inv [n] DI02 status | 32-bit bitfield | 4 | 1 | IREG_15129.1 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI02_status |  | Need schematic to tell us what function each DI has
280 |  | Counter | Inv [n] DI03 status | 32-bit bitfield | 4 | 2 | IREG_15129.2 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI03_status |  | Need schematic to tell us what function each DI has
281 |  | Counter | Inv [n] DI04 status | 32-bit bitfield | 4 | 3 | IREG_15129.3 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI04_status |  | Need schematic to tell us what function each DI has
282 |  | Counter | Inv [n] DI05 status | 32-bit bitfield | 4 | 4 | IREG_15129.4 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI05_status
283 |  | Counter | Inv [n] DI06 status | 32-bit bitfield | 4 | 5 | IREG_15129.5 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI06_status
284 |  | Counter | Inv [n] DI07 status | 32-bit bitfield | 4 | 6 | IREG_15129.6 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI07_status
285 |  | Counter | Inv [n] DI08 status | 32-bit bitfield | 4 | 7 | IREG_15129.7 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI08_status
286 |  | Counter | Inv [n] DI09 status | 32-bit bitfield | 4 | 8 | IREG_15129.8 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI09_status
287 |  | Counter | Inv [n] DI10 status | 32-bit bitfield | 4 | 9 | IREG_15129.9 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI10_status
288 |  | Counter | Inv [n] DI11 status | 32-bit bitfield | 4 | 10 | IREG_15129.10 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI11_status
289 |  | Counter | Inv [n] DI12 status | 32-bit bitfield | 4 | 11 | IREG_15129.11 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI12_status
290 |  | Counter | Inv [n] DI13 status | 32-bit bitfield | 4 | 12 | IREG_15129.12 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI13_status
291 |  | Counter | Inv [n] DI14 status | 32-bit bitfield | 4 | 13 | IREG_15129.13 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI14_status
292 |  | Counter | Inv [n] DI15 status | 32-bit bitfield | 4 | 14 | IREG_15129.14 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI15_status
293 |  | Counter | Inv [n] DI16 status | 32-bit bitfield | 4 | 15 | IREG_15129.15 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI16_status
294 |  | Counter | Inv [n] DI17 status | 32-bit bitfield | 4 | 16 | IREG_15129.16 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI17_status
295 |  | Counter | Inv [n] DI18 status | 32-bit bitfield | 4 | 17 | IREG_15129.17 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI18_status
296 |  | Counter | Inv [n] DI19 status | 32-bit bitfield | 4 | 18 | IREG_15129.18 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI19_status
297 |  | Counter | Inv [n] DI20 status | 32-bit bitfield | 4 | 19 | IREG_15129.19 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI20_status
298 |  | Counter | Inv [n] DI21 status | 32-bit bitfield | 4 | 20 | IREG_15129.20 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI21_status
299 |  | Counter | Inv [n] DI22 status | 32-bit bitfield | 4 | 21 | IREG_15129.21 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI22_status
300 |  | Counter | Inv [n] DI23 status | 32-bit bitfield | 4 | 22 | IREG_15129.22 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI23_status
301 |  | Counter | Inv [n] DI24 status | 32-bit bitfield | 4 | 23 | IREG_15129.23 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0004_Inv_[n]_DI24_status
302 |  | Counter | Inv [n] PMD IO register | 32-bit bitfield | 5 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0005_Inv_[n]_PMD_IO_register
303 |  | Counter | Inv [n] PMD DI01 status | 32-bit bitfield | 5 | 0 | IREG_15142.0 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI01_status
304 |  | Counter | Inv [n] PMD DI02 status | 32-bit bitfield | 5 | 1 | IREG_15142.1 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI02_status
305 |  | Counter | Inv [n] PMD DI03 status | 32-bit bitfield | 5 | 2 | IREG_15142.2 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI03_status
306 | Available | Counter | Inv [n] PMD DI04 status | 32-bit bitfield | 5 | 3 | IREG_15142.3 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI04_status
307 | Available | Counter | Inv [n] PMD DI05 status | 32-bit bitfield | 5 | 4 | IREG_15142.4 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI05_status
308 | Available | Counter | Inv [n] PMD DI06 status | 32-bit bitfield | 5 | 5 | IREG_15142.5 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI06_status
309 | Available | Counter | Inv [n] PMD DI07 status | 32-bit bitfield | 5 | 6 | IREG_15142.6 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI07_status
310 | Available | Counter | Inv [n] PMD DI08 status | 32-bit bitfield | 5 | 7 | IREG_15142.7 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI08_status
311 | Available | Counter | Inv [n] PMD DI09 status | 32-bit bitfield | 5 | 8 | IREG_15142.8 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI09_status
312 | Available | Counter | Inv [n] PMD DI10 status | 32-bit bitfield | 5 | 9 | IREG_15142.9 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI10_status
313 | Available | Counter | Inv [n] PMD DI11 status | 32-bit bitfield | 5 | 10 | IREG_15142.10 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI11_status
314 | Available | Counter | Inv [n] PMD DI12 status | 32-bit bitfield | 5 | 11 | IREG_15142.11 | None | On | Off | [8 empty] | Change events | Diagnostic | CNT_0005_Inv_[n]_PMD_DI12_status
315 |  | Counter | Inv [n] unit 1 status register | 32-bit bitfield | 10 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0010_Inv_[n]_unit_1_status_register
316 | Available | Counter | Inv [n] unit 1 Unit is running | 32-bit bitfield | 10 | 0 | IREG_15208.17 | None | Running | Stopped | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Unit_is_running
317 | Available | Counter | Inv [n] unit 1 Unit is stopped | 32-bit bitfield | 10 | 1 | IREG_15208.18 | None | Stopped | Running | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Unit_is_stopped
318 | Available | Counter | Inv [n] unit 1 Run | 32-bit bitfield | 10 | 2 | IREG_15208.0 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Run
319 | Available | Counter | Inv [n] unit 1 Stop | 32-bit bitfield | 10 | 3 | IREG_15208.1 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Stop
320 | Available | Counter | Inv [n] unit 1 Initial standby | 32-bit bitfield | 10 | 4 | IREG_15208.2 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Initial_standby
321 | Available | Counter | Inv [n] unit 1 Press to shutdown | 32-bit bitfield | 10 | 5 | IREG_15208.3 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Press_to_shutdown
322 | Available | Counter | Inv [n] unit 1 Standby | 32-bit bitfield | 10 | 6 | IREG_15208.4 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Standby
323 | Available | Counter | Inv [n] unit 1 Emergency stop | 32-bit bitfield | 10 | 7 | IREG_15208.5 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Emergency_stop
324 | Available | Counter | Inv [n] unit 1 Starting up | 32-bit bitfield | 10 | 8 | IREG_15208.6 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Starting_up
325 | Available | Counter | Inv [n] unit 1 Shutting down | 32-bit bitfield | 10 | 9 | IREG_15208.7 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Shutting_down
326 | Available | Counter | Inv [n] unit 1 Shut down | 32-bit bitfield | 10 | 10 | IREG_15208.9 | None | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Shut_down
327 | Available | Counter | Inv [n] unit 1 Warning run | 32-bit bitfield | 10 | 11 | IREG_15208.10 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Warning_run
328 | Available | Counter | Inv [n] unit 1 Derating run | 32-bit bitfield | 10 | 12 | IREG_15208.11 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Derating_run
329 | Available | Counter | Inv [n] unit 1 IO and DSP communication error | 32-bit bitfield | 10 | 13 | IREG_15208.13 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_IO_and_DSP_communication_error
330 | Available | Counter | Inv [n] unit 1 Anti-PID run | 32-bit bitfield | 10 | 14 | IREG_15208.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Anti_PID_run
331 | Available | Counter | Inv [n] unit 1 AC breaker status | 32-bit bitfield | 10 | 15 | IREG_15194.0 | None | Closed | Open | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_AC_breaker_status
332 | Available | Counter | Inv [n] unit 1 DC switch 1 status | 32-bit bitfield | 10 | 16 | IREG_15194.3 | None | Closed | Open | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_DC_switch_1_status
333 | Available | Counter | Inv [n] unit 1 Emergency shutdown node | 32-bit bitfield | 10 | 17 | IREG_15194.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0010_Inv_[n]_unit_1_Emergency_shutdown_node
334 |  | Counter | Inv [n] unit 1 faults register 1 | 32-bit bitfield | 11 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0011_Inv_[n]_unit_1_faults_register_1
335 | Available | Counter | Inv [n] unit 1 Smoke node | 32-bit bitfield | 11 | 0 | IREG_15194.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Smoke_node
336 | Available | Counter | Inv [n] unit 1 Access node | 32-bit bitfield | 11 | 1 | IREG_15194.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Access_node
337 | Available | Counter | Inv [n] unit 1 DC undervoltage fault | 32-bit bitfield | 11 | 2 | IREG_15186.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_undervoltage_fault
338 | Available | Counter | Inv [n] unit 1 DC overvoltage fault | 32-bit bitfield | 11 | 3 | IREG_15186.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_overvoltage_fault
339 | Available | Counter | Inv [n] unit 1 AC undervoltage fault | 32-bit bitfield | 11 | 4 | IREG_15186.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_AC_undervoltage_fault
340 | Available | Counter | Inv [n] unit 1 AC overvoltage fault | 32-bit bitfield | 11 | 5 | IREG_15186.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_AC_overvoltage_fault
341 | Available | Counter | Inv [n] unit 1 Anti islanding protection active | 32-bit bitfield | 11 | 6 | IREG_15186.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Anti_islanding_protection_active
342 | Available | Counter | Inv [n] unit 1 PDP protection active | 32-bit bitfield | 11 | 7 | IREG_15186.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_PDP_protection_active
343 | Available | Counter | Inv [n] unit 1 Module overtemperature fault | 32-bit bitfield | 11 | 8 | IREG_15186.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Module_overtemperature_fault
344 | Available | Counter | Inv [n] unit 1 Reactor overtemperature fault | 32-bit bitfield | 11 | 9 | IREG_15186.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Reactor_overtemperature_fault
345 | Available | Counter | Inv [n] unit 1 AC leakage current protection fault | 32-bit bitfield | 11 | 10 | IREG_15186.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_AC_leakage_current_protection_fault
346 | Available | Counter | Inv [n] unit 1 GFDI protection active | 32-bit bitfield | 11 | 11 | IREG_15186.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_GFDI_protection_active
347 | Available | Counter | Inv [n] unit 1 Fan 1 fault | 32-bit bitfield | 11 | 12 | IREG_15186.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Fan_1_fault
348 | Available | Counter | Inv [n] unit 1 DC overcurrent | 32-bit bitfield | 11 | 13 | IREG_15186.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_overcurrent
349 | Available | Counter | Inv [n] unit 1 AC overcurrent | 32-bit bitfield | 11 | 14 | IREG_15186.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_AC_overcurrent
350 | Available | Counter | Inv [n] unit 1 Frequency abnormal | 32-bit bitfield | 11 | 15 | IREG_15186.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Frequency_abnormal
351 | Available | Counter | Inv [n] unit 1 Temperature abnormal | 32-bit bitfield | 11 | 16 | IREG_15186.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Temperature_abnormal
352 | Available | Counter | Inv [n] unit 1 Hardware fault | 32-bit bitfield | 11 | 17 | IREG_15186.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Hardware_fault
353 | Available | Counter | Inv [n] unit 1 Grounding fault | 32-bit bitfield | 11 | 18 | IREG_15186.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Grounding_fault
354 | Available | Counter | Inv [n] unit 1 Bus overvoltage | 32-bit bitfield | 11 | 19 | IREG_15186.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Bus_overvoltage
355 | Available | Counter | Inv [n] unit 1 Bus undervoltage | 32-bit bitfield | 11 | 20 | IREG_15186.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Bus_undervoltage
356 | Available | Counter | Inv [n] unit 1 Inverter overvoltage | 32-bit bitfield | 11 | 21 | IREG_15186.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Inverter_overvoltage
357 | Available | Counter | Inv [n] unit 1 Low insulation resistance fault | 32-bit bitfield | 11 | 22 | IREG_15188.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Low_insulation_resistance_fault
358 | Available | Counter | Inv [n] unit 1 AC SPD fault | 32-bit bitfield | 11 | 23 | IREG_15188.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_AC_SPD_fault
359 | Available | Counter | Inv [n] unit 1 Sampling fault | 32-bit bitfield | 11 | 24 | IREG_15188.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Sampling_fault
360 | Available | Counter | Inv [n] unit 1 DC polarity reversed fault | 32-bit bitfield | 11 | 25 | IREG_15188.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_polarity_reversed_fault
361 | Available | Counter | Inv [n] unit 1 Control power supply fault | 32-bit bitfield | 11 | 26 | IREG_15188.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Control_power_supply_fault
362 | Available | Counter | Inv [n] unit 1 AC current imballance | 32-bit bitfield | 11 | 27 | IREG_15188.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_AC_current_imballance
363 | Available | Counter | Inv [n] unit 1 DC SPD fault | 32-bit bitfield | 11 | 28 | IREG_15188.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_SPD_fault
364 | Available | Counter | Inv [n] unit 1 DC component fault | 32-bit bitfield | 11 | 29 | IREG_15188.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_component_fault
365 | Available | Counter | Inv [n] unit 1 DC switch fault | 32-bit bitfield | 11 | 30 | IREG_15188.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_DC_switch_fault
366 | Available | Counter | Inv [n] unit 1 Repeated fault | 32-bit bitfield | 11 | 31 | IREG_15188.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0011_Inv_[n]_unit_1_Repeated_fault
367 |  | Counter | Inv [n] unit 1 faults register 2 | 32-bit bitfield | 12 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0012_Inv_[n]_unit_1_faults_register_2
368 | Available | Counter | Inv [n] unit 1 Parallel operation communication failure | 32-bit bitfield | 12 | 0 | IREG_15188.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Parallel_operation_communication_failure
369 | Available | Counter | Inv [n] unit 1 Control cabinet temperature fault | 32-bit bitfield | 12 | 1 | IREG_15188.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Control_cabinet_temperature_fault
370 | Available | Counter | Inv [n] unit 1 DC fuse ground fault | 32-bit bitfield | 12 | 2 | IREG_15188.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_DC_fuse_ground_fault
371 | Available | Counter | Inv [n] unit 1 Excessive DC reverse current fault | 32-bit bitfield | 12 | 3 | IREG_15188.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Excessive_DC_reverse_current_fault
372 | Available | Counter | Inv [n] unit 1 Grid voltage imballance fault | 32-bit bitfield | 12 | 4 | IREG_15188.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Grid_voltage_imballance_fault
373 | Available | Counter | Inv [n] unit 1 Inverter cabinet temperature fault | 32-bit bitfield | 12 | 5 | IREG_15188.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Inverter_cabinet_temperature_fault
374 | Available | Counter | Inv [n] unit 1 AC cabinet temperature fault | 32-bit bitfield | 12 | 6 | IREG_15188.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_AC_cabinet_temperature_fault
375 | Available | Counter | Inv [n] unit 1 AC switch off | 32-bit bitfield | 12 | 7 | IREG_15188.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_AC_switch_off
376 | Available | Counter | Inv [n] unit 1 AC switch fault | 32-bit bitfield | 12 | 8 | IREG_15188.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_AC_switch_fault
377 | Available | Counter | Inv [n] unit 1 Soft start fault | 32-bit bitfield | 12 | 9 | IREG_15188.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Soft_start_fault
378 | Available | Counter | Inv [n] unit 1 DC voltage sampling fault | 32-bit bitfield | 12 | 10 | IREG_15188.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_DC_voltage_sampling_fault
379 | Available | Counter | Inv [n] unit 1 Fan 2 fault | 32-bit bitfield | 12 | 11 | IREG_15188.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Fan_2_fault
380 | Available | Counter | Inv [n] unit 1 Current unbalance 2 | 32-bit bitfield | 12 | 12 | IREG_15188.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Current_unbalance_2
381 | Available | Counter | Inv [n] unit 1 Current unbalance 3 | 32-bit bitfield | 12 | 13 | IREG_15188.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Current_unbalance_3
382 | Available | Counter | Inv [n] unit 1 DC cabinet temperature alarm | 32-bit bitfield | 12 | 14 | IREG_15188.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_DC_cabinet_temperature_alarm
383 | Available | Counter | Inv [n] unit 1 Neutral point potential shift alarm | 32-bit bitfield | 12 | 15 | IREG_15188.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Neutral_point_potential_shift_alarm
384 | Available | Counter | Inv [n] unit 1 Carrier sync failure | 32-bit bitfield | 12 | 16 | IREG_15188.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Carrier_sync_failure
385 | Available | Counter | Inv [n] unit 1 Smoke alarm | 32-bit bitfield | 12 | 17 | IREG_15190.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Smoke_alarm
386 | Available | Counter | Inv [n] unit 1 Access control protection alarm | 32-bit bitfield | 12 | 18 | IREG_15190.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Access_control_protection_alarm
387 | Available | Counter | Inv [n] unit 1 Emergency shutdown alarm | 32-bit bitfield | 12 | 19 | IREG_15190.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0012_Inv_[n]_unit_1_Emergency_shutdown_alarm
388 |  | Counter | Inv [n] unit 1 alarms register | 32-bit bitfield | 13 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0013_Inv_[n]_unit_1_alarms_register
389 | Available | Counter | Inv [n] unit 1 Temperature abnormal alarm | 32-bit bitfield | 13 | 0 | IREG_15210.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Temperature_abnormal_alarm
390 | Available | Counter | Inv [n] unit 1 Low insulation resistance alarm | 32-bit bitfield | 13 | 1 | IREG_15210.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Low_insulation_resistance_alarm
391 | Available | Counter | Inv [n] unit 1 GFRT operation alarm | 32-bit bitfield | 13 | 2 | IREG_15210.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_GFRT_operation_alarm
392 | Available | Counter | Inv [n] unit 1 CT unbalance alarm | 32-bit bitfield | 13 | 3 | IREG_15210.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_CT_unbalance_alarm
393 | Available | Counter | Inv [n] unit 1 DC sensor alarm | 32-bit bitfield | 13 | 4 | IREG_15210.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_DC_sensor_alarm
394 | Available | Counter | Inv [n] unit 1 DC SPD alarm | 32-bit bitfield | 13 | 5 | IREG_15210.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_DC_SPD_alarm
395 | Available | Counter | Inv [n] unit 1 AC SPD alarm | 32-bit bitfield | 13 | 6 | IREG_15210.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_AC_SPD_alarm
396 | Available | Counter | Inv [n] unit 1 DC switch alarm | 32-bit bitfield | 13 | 7 | IREG_15210.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_DC_switch_alarm
397 | Available | Counter | Inv [n] unit 1 Anti-PID power alarm | 32-bit bitfield | 13 | 8 | IREG_15210.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Anti_PID_power_alarm
398 | Available | Counter | Inv [n] unit 1 Cooling fan 1 alarm | 32-bit bitfield | 13 | 9 | IREG_15210.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Cooling_fan_1_alarm
399 | Available | Counter | Inv [n] unit 1 DC branch forward alarm | 32-bit bitfield | 13 | 10 | IREG_15210.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_DC_branch_forward_alarm
400 | Available | Counter | Inv [n] unit 1 DC branch reverse alarm | 32-bit bitfield | 13 | 11 | IREG_15210.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_DC_branch_reverse_alarm
401 | Available | Counter | Inv [n] unit 1 AC switch alarm | 32-bit bitfield | 13 | 12 | IREG_15210.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_AC_switch_alarm
402 | Available | Counter | Inv [n] unit 1 Meter communication failure alarm | 32-bit bitfield | 13 | 13 | IREG_15210.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Meter_communication_failure_alarm
403 | Available | Counter | Inv [n] unit 1 Cooling fan 2 alarm | 32-bit bitfield | 13 | 14 | IREG_15210.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Cooling_fan_2_alarm
404 | Available | Counter | Inv [n] unit 1 Temperature and humidity sensor alarm | 32-bit bitfield | 13 | 15 | IREG_15210.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Temperature_and_humidity_sensor_alarm
405 | Available | Counter | Inv [n] unit 1 Frequency deviation active power regulation | 32-bit bitfield | 13 | 16 | IREG_15210.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Frequency_deviation_active_power_regulation
406 | Available | Counter | Inv [n] unit 1 Voltage deviation reactive power regulation | 32-bit bitfield | 13 | 17 | IREG_15210.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Voltage_deviation_reactive_power_regulation
407 | Available | Counter | Inv [n] unit 1 Busbar temperature alarm | 32-bit bitfield | 13 | 18 | IREG_15210.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Busbar_temperature_alarm
408 | Available | Counter | Inv [n] unit 1 Cooling fan derating alarm | 32-bit bitfield | 13 | 19 | IREG_15210.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Cooling_fan_derating_alarm
409 | Available | Counter | Inv [n] unit 1 Frequency abnormal | 32-bit bitfield | 13 | 20 | IREG_15210.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_Frequency_abnormal
410 | Available | Counter | Inv [n] unit 1 HVRT operation | 32-bit bitfield | 13 | 21 | IREG_15262.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_HVRT_operation
411 | Available | Counter | Inv [n] unit 1 LVRT operation | 32-bit bitfield | 13 | 22 | IREG_15262.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0013_Inv_[n]_unit_1_LVRT_operation
412 |  | Counter | Inv [n] unit 1 array monitoring register | 32-bit bitfield | 14 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0014_Inv_[n]_unit_1_array_monitoring_register
413 |  | Counter | Inv [n] unit 1 DC input 1 open circuit fault | 32-bit bitfield | 14 | 1 | IREG_16001.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_1_open_circuit_fault
414 |  | Counter | Inv [n] unit 1 DC input 2 open circuit fault | 32-bit bitfield | 14 | 2 | IREG_16001.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_2_open_circuit_fault
415 |  | Counter | Inv [n] unit 1 DC input 3 open circuit fault | 32-bit bitfield | 14 | 3 | IREG_16001.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_3_open_circuit_fault
416 |  | Counter | Inv [n] unit 1 DC input 4 open circuit fault | 32-bit bitfield | 14 | 4 | IREG_16001.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_4_open_circuit_fault
417 |  | Counter | Inv [n] unit 1 DC input 5 open circuit fault | 32-bit bitfield | 14 | 5 | IREG_16001.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_5_open_circuit_fault
418 |  | Counter | Inv [n] unit 1 DC input 6 open circuit fault | 32-bit bitfield | 14 | 6 | IREG_16001.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_6_open_circuit_fault
419 |  | Counter | Inv [n] unit 1 DC input 7 open circuit fault | 32-bit bitfield | 14 | 7 | IREG_16001.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_7_open_circuit_fault
420 |  | Counter | Inv [n] unit 1 DC input 1 string failure alarm | 32-bit bitfield | 14 | 11 | IREG_16003.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_1_string_failure_alarm
421 |  | Counter | Inv [n] unit 1 DC input 2 string failure alarm | 32-bit bitfield | 14 | 12 | IREG_16003.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_2_string_failure_alarm
422 |  | Counter | Inv [n] unit 1 DC input 3 string failure alarm | 32-bit bitfield | 14 | 13 | IREG_16003.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_3_string_failure_alarm
423 |  | Counter | Inv [n] unit 1 DC input 4 string failure alarm | 32-bit bitfield | 14 | 14 | IREG_16003.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_4_string_failure_alarm
424 |  | Counter | Inv [n] unit 1 DC input 5 string failure alarm | 32-bit bitfield | 14 | 15 | IREG_16003.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_5_string_failure_alarm
425 |  | Counter | Inv [n] unit 1 DC input 6 string failure alarm | 32-bit bitfield | 14 | 16 | IREG_16003.5 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_6_string_failure_alarm
426 |  | Counter | Inv [n] unit 1 DC input 7 string failure alarm | 32-bit bitfield | 14 | 17 | IREG_16003.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0014_Inv_[n]_unit_1_DC_input_7_string_failure_alarm
427 | Available | Counter | Inv [n] unit 2 status register | 32-bit bitfield | 20 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0020_Inv_[n]_unit_2_status_register
428 | Available | Counter | Inv [n] unit 2 Unit is running | 32-bit bitfield | 20 | 0 | IREG_15328.17 | None | Running | Stopped | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Unit_is_running
429 | Available | Counter | Inv [n] unit 2 Unit is stopped | 32-bit bitfield | 20 | 1 | IREG_15328.18 | None | Stopped | Running | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Unit_is_stopped
430 | Available | Counter | Inv [n] unit 2 Run | 32-bit bitfield | 20 | 2 | IREG_15328.0 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Run
431 | Available | Counter | Inv [n] unit 2 Stop | 32-bit bitfield | 20 | 3 | IREG_15328.1 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Stop
432 | Available | Counter | Inv [n] unit 2 Initial standby | 32-bit bitfield | 20 | 4 | IREG_15328.2 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Initial_standby
433 | Available | Counter | Inv [n] unit 2 Press to shutdown | 32-bit bitfield | 20 | 5 | IREG_15328.3 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Press_to_shutdown
434 | Available | Counter | Inv [n] unit 2 Standby | 32-bit bitfield | 20 | 6 | IREG_15328.4 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Standby
435 | Available | Counter | Inv [n] unit 2 Emergency stop | 32-bit bitfield | 20 | 7 | IREG_15328.5 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Emergency_stop
436 | Available | Counter | Inv [n] unit 2 Starting up | 32-bit bitfield | 20 | 8 | IREG_15328.6 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Starting_up
437 | Available | Counter | Inv [n] unit 2 Shutting down | 32-bit bitfield | 20 | 9 | IREG_15328.7 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Shutting_down
438 | Available | Counter | Inv [n] unit 2 Shut down | 32-bit bitfield | 20 | 10 | IREG_15328.9 | None | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Shut_down
439 | Available | Counter | Inv [n] unit 2 Warning run | 32-bit bitfield | 20 | 11 | IREG_15328.10 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Warning_run
440 | Available | Counter | Inv [n] unit 2 Derating run | 32-bit bitfield | 20 | 12 | IREG_15328.11 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Derating_run
441 | Available | Counter | Inv [n] unit 2 IO and DSP communication error | 32-bit bitfield | 20 | 13 | IREG_15328.13 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_IO_and_DSP_communication_error
442 | Available | Counter | Inv [n] unit 2 Anti-PID run | 32-bit bitfield | 20 | 14 | IREG_15328.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Anti_PID_run
443 | Available | Counter | Inv [n] unit 2 AC breaker status | 32-bit bitfield | 20 | 15 | IREG_15314.0 | None | Closed | Open | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_AC_breaker_status
444 | Available | Counter | Inv [n] unit 2 DC switch 1 status | 32-bit bitfield | 20 | 16 | IREG_15314.3 | None | Closed | Open | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_DC_switch_1_status
445 | Available | Counter | Inv [n] unit 2 Emergency shutdown node | 32-bit bitfield | 20 | 17 | IREG_15314.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0020_Inv_[n]_unit_2_Emergency_shutdown_node
446 | Available | Counter | Inv [n] unit 2 faults register 1 | 32-bit bitfield | 21 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0021_Inv_[n]_unit_2_faults_register_1
447 | Available | Counter | Inv [n] unit 2 Smoke node | 32-bit bitfield | 21 | 0 | IREG_15314.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Smoke_node
448 | Available | Counter | Inv [n] unit 2 Access node | 32-bit bitfield | 21 | 1 | IREG_15314.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Access_node
449 | Available | Counter | Inv [n] unit 2 DC undervoltage fault | 32-bit bitfield | 21 | 2 | IREG_15306.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_undervoltage_fault
450 | Available | Counter | Inv [n] unit 2 DC overvoltage fault | 32-bit bitfield | 21 | 3 | IREG_15306.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_overvoltage_fault
451 | Available | Counter | Inv [n] unit 2 AC undervoltage fault | 32-bit bitfield | 21 | 4 | IREG_15306.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_AC_undervoltage_fault
452 | Available | Counter | Inv [n] unit 2 AC overvoltage fault | 32-bit bitfield | 21 | 5 | IREG_15306.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_AC_overvoltage_fault
453 | Available | Counter | Inv [n] unit 2 Anti islanding protection active | 32-bit bitfield | 21 | 6 | IREG_15306.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Anti_islanding_protection_active
454 | Available | Counter | Inv [n] unit 2 PDP protection active | 32-bit bitfield | 21 | 7 | IREG_15306.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_PDP_protection_active
455 | Available | Counter | Inv [n] unit 2 Module overtemperature fault | 32-bit bitfield | 21 | 8 | IREG_15306.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Module_overtemperature_fault
456 | Available | Counter | Inv [n] unit 2 Reactor overtemperature fault | 32-bit bitfield | 21 | 9 | IREG_15306.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Reactor_overtemperature_fault
457 | Available | Counter | Inv [n] unit 2 AC leakage current protection fault | 32-bit bitfield | 21 | 10 | IREG_15306.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_AC_leakage_current_protection_fault
458 | Available | Counter | Inv [n] unit 2 GFDI protection active | 32-bit bitfield | 21 | 11 | IREG_15306.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_GFDI_protection_active
459 | Available | Counter | Inv [n] unit 2 Fan 1 fault | 32-bit bitfield | 21 | 12 | IREG_15306.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Fan_1_fault
460 | Available | Counter | Inv [n] unit 2 DC overcurrent | 32-bit bitfield | 21 | 13 | IREG_15306.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_overcurrent
461 | Available | Counter | Inv [n] unit 2 AC overcurrent | 32-bit bitfield | 21 | 14 | IREG_15306.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_AC_overcurrent
462 | Available | Counter | Inv [n] unit 2 Frequency abnormal | 32-bit bitfield | 21 | 15 | IREG_15306.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Frequency_abnormal
463 | Available | Counter | Inv [n] unit 2 Temperature abnormal | 32-bit bitfield | 21 | 16 | IREG_15306.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Temperature_abnormal
464 | Available | Counter | Inv [n] unit 2 Hardware fault | 32-bit bitfield | 21 | 17 | IREG_15306.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Hardware_fault
465 | Available | Counter | Inv [n] unit 2 Grounding fault | 32-bit bitfield | 21 | 18 | IREG_15306.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Grounding_fault
466 | Available | Counter | Inv [n] unit 2 Bus overvoltage | 32-bit bitfield | 21 | 19 | IREG_15306.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Bus_overvoltage
467 | Available | Counter | Inv [n] unit 2 Bus undervoltage | 32-bit bitfield | 21 | 20 | IREG_15306.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Bus_undervoltage
468 | Available | Counter | Inv [n] unit 2 Inverter overvoltage | 32-bit bitfield | 21 | 21 | IREG_15306.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Inverter_overvoltage
469 | Available | Counter | Inv [n] unit 2 Low insulation resistance fault | 32-bit bitfield | 21 | 22 | IREG_15308.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Low_insulation_resistance_fault
470 | Available | Counter | Inv [n] unit 2 AC SPD fault | 32-bit bitfield | 21 | 23 | IREG_15308.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_AC_SPD_fault
471 | Available | Counter | Inv [n] unit 2 Sampling fault | 32-bit bitfield | 21 | 24 | IREG_15308.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Sampling_fault
472 | Available | Counter | Inv [n] unit 2 DC polarity reversed fault | 32-bit bitfield | 21 | 25 | IREG_15308.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_polarity_reversed_fault
473 | Available | Counter | Inv [n] unit 2 Control power supply fault | 32-bit bitfield | 21 | 26 | IREG_15308.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Control_power_supply_fault
474 | Available | Counter | Inv [n] unit 2 AC current imballance | 32-bit bitfield | 21 | 27 | IREG_15308.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_AC_current_imballance
475 | Available | Counter | Inv [n] unit 2 DC SPD fault | 32-bit bitfield | 21 | 28 | IREG_15308.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_SPD_fault
476 | Available | Counter | Inv [n] unit 2 DC component fault | 32-bit bitfield | 21 | 29 | IREG_15308.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_component_fault
477 | Available | Counter | Inv [n] unit 2 DC switch fault | 32-bit bitfield | 21 | 30 | IREG_15308.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_DC_switch_fault
478 | Available | Counter | Inv [n] unit 2 Repeated fault | 32-bit bitfield | 21 | 31 | IREG_15308.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0021_Inv_[n]_unit_2_Repeated_fault
479 | Available | Counter | Inv [n] unit 2 faults register 2 | 32-bit bitfield | 22 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0022_Inv_[n]_unit_2_faults_register_2
480 | Available | Counter | Inv [n] unit 2 Parallel operation communication failure | 32-bit bitfield | 22 | 0 | IREG_15308.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Parallel_operation_communication_failure
481 | Available | Counter | Inv [n] unit 2 Control cabinet temperature fault | 32-bit bitfield | 22 | 1 | IREG_15308.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Control_cabinet_temperature_fault
482 | Available | Counter | Inv [n] unit 2 DC fuse ground fault | 32-bit bitfield | 22 | 2 | IREG_15308.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_DC_fuse_ground_fault
483 | Available | Counter | Inv [n] unit 2 Excessive DC reverse current fault | 32-bit bitfield | 22 | 3 | IREG_15308.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Excessive_DC_reverse_current_fault
484 | Available | Counter | Inv [n] unit 2 Grid voltage imballance fault | 32-bit bitfield | 22 | 4 | IREG_15308.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Grid_voltage_imballance_fault
485 | Available | Counter | Inv [n] unit 2 Inverter cabinet temperature fault | 32-bit bitfield | 22 | 5 | IREG_15308.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Inverter_cabinet_temperature_fault
486 | Available | Counter | Inv [n] unit 2 AC cabinet temperature fault | 32-bit bitfield | 22 | 6 | IREG_15308.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_AC_cabinet_temperature_fault
487 | Available | Counter | Inv [n] unit 2 AC switch off | 32-bit bitfield | 22 | 7 | IREG_15308.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_AC_switch_off
488 | Available | Counter | Inv [n] unit 2 AC switch fault | 32-bit bitfield | 22 | 8 | IREG_15308.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_AC_switch_fault
489 | Available | Counter | Inv [n] unit 2 Soft start fault | 32-bit bitfield | 22 | 9 | IREG_15308.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Soft_start_fault
490 | Available | Counter | Inv [n] unit 2 DC voltage sampling fault | 32-bit bitfield | 22 | 10 | IREG_15308.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_DC_voltage_sampling_fault
491 | Available | Counter | Inv [n] unit 2 Fan 2 fault | 32-bit bitfield | 22 | 11 | IREG_15308.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Fan_2_fault
492 | Available | Counter | Inv [n] unit 2 Current unbalance 2 | 32-bit bitfield | 22 | 12 | IREG_15308.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Current_unbalance_2
493 | Available | Counter | Inv [n] unit 2 Current unbalance 3 | 32-bit bitfield | 22 | 13 | IREG_15308.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Current_unbalance_3
494 | Available | Counter | Inv [n] unit 2 DC cabinet temperature alarm | 32-bit bitfield | 22 | 14 | IREG_15308.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_DC_cabinet_temperature_alarm
495 | Available | Counter | Inv [n] unit 2 Neutral point potential shift alarm | 32-bit bitfield | 22 | 15 | IREG_15308.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Neutral_point_potential_shift_alarm
496 | Available | Counter | Inv [n] unit 2 Carrier sync failure | 32-bit bitfield | 22 | 16 | IREG_15308.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Carrier_sync_failure
497 | Available | Counter | Inv [n] unit 2 Smoke alarm | 32-bit bitfield | 22 | 17 | IREG_15310.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Smoke_alarm
498 | Available | Counter | Inv [n] unit 2 Access control protection alarm | 32-bit bitfield | 22 | 18 | IREG_15310.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Access_control_protection_alarm
499 | Available | Counter | Inv [n] unit 2 Emergency shutdown alarm | 32-bit bitfield | 22 | 19 | IREG_15310.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0022_Inv_[n]_unit_2_Emergency_shutdown_alarm
500 | Available | Counter | Inv [n] unit 2 alarms register | 32-bit bitfield | 23 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0023_Inv_[n]_unit_2_alarms_register
501 | Available | Counter | Inv [n] unit 2 Temperature abnormal alarm | 32-bit bitfield | 23 | 0 | IREG_15330.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Temperature_abnormal_alarm
502 | Available | Counter | Inv [n] unit 2 Low insulation resistance alarm | 32-bit bitfield | 23 | 1 | IREG_15330.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Low_insulation_resistance_alarm
503 | Available | Counter | Inv [n] unit 2 GFRT operation alarm | 32-bit bitfield | 23 | 2 | IREG_15330.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_GFRT_operation_alarm
504 | Available | Counter | Inv [n] unit 2 CT unbalance alarm | 32-bit bitfield | 23 | 3 | IREG_15330.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_CT_unbalance_alarm
505 | Available | Counter | Inv [n] unit 2 DC sensor alarm | 32-bit bitfield | 23 | 4 | IREG_15330.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_DC_sensor_alarm
506 | Available | Counter | Inv [n] unit 2 DC SPD alarm | 32-bit bitfield | 23 | 5 | IREG_15330.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_DC_SPD_alarm
507 | Available | Counter | Inv [n] unit 2 AC SPD alarm | 32-bit bitfield | 23 | 6 | IREG_15330.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_AC_SPD_alarm
508 | Available | Counter | Inv [n] unit 2 DC switch alarm | 32-bit bitfield | 23 | 7 | IREG_15330.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_DC_switch_alarm
509 | Available | Counter | Inv [n] unit 2 Anti-PID power alarm | 32-bit bitfield | 23 | 8 | IREG_15330.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Anti_PID_power_alarm
510 | Available | Counter | Inv [n] unit 2 Cooling fan 1 alarm | 32-bit bitfield | 23 | 9 | IREG_15330.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Cooling_fan_1_alarm
511 | Available | Counter | Inv [n] unit 2 DC branch forward alarm | 32-bit bitfield | 23 | 10 | IREG_15330.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_DC_branch_forward_alarm
512 | Available | Counter | Inv [n] unit 2 DC branch reverse alarm | 32-bit bitfield | 23 | 11 | IREG_15330.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_DC_branch_reverse_alarm
513 | Available | Counter | Inv [n] unit 2 AC switch alarm | 32-bit bitfield | 23 | 12 | IREG_15330.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_AC_switch_alarm
514 | Available | Counter | Inv [n] unit 2 Meter communication failure alarm | 32-bit bitfield | 23 | 13 | IREG_15330.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Meter_communication_failure_alarm
515 | Available | Counter | Inv [n] unit 2 Cooling fan 2 alarm | 32-bit bitfield | 23 | 14 | IREG_15330.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Cooling_fan_2_alarm
516 | Available | Counter | Inv [n] unit 2 Temperature and humidity sensor alarm | 32-bit bitfield | 23 | 15 | IREG_15330.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Temperature_and_humidity_sensor_alarm
517 | Available | Counter | Inv [n] unit 2 Frequency deviation active power regulation | 32-bit bitfield | 23 | 16 | IREG_15330.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Frequency_deviation_active_power_regulation
518 | Available | Counter | Inv [n] unit 2 Voltage deviation reactive power regulation | 32-bit bitfield | 23 | 17 | IREG_15330.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Voltage_deviation_reactive_power_regulation
519 | Available | Counter | Inv [n] unit 2 Busbar temperature alarm | 32-bit bitfield | 23 | 18 | IREG_15330.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Busbar_temperature_alarm
520 | Available | Counter | Inv [n] unit 2 Cooling fan derating alarm | 32-bit bitfield | 23 | 19 | IREG_15330.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Cooling_fan_derating_alarm
521 | Available | Counter | Inv [n] unit 2 Frequency abnormal | 32-bit bitfield | 23 | 20 | IREG_15330.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_Frequency_abnormal
522 | Available | Counter | Inv [n] unit 2 HVRT operation | 32-bit bitfield | 23 | 21 | IREG_15382.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_HVRT_operation
523 | Available | Counter | Inv [n] unit 2 LVRT operation | 32-bit bitfield | 23 | 22 | IREG_15382.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0023_Inv_[n]_unit_2_LVRT_operation
524 |  | Counter | Inv [n] unit 2 array monitoring register | 32-bit bitfield | 24 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0024_Inv_[n]_unit_2_array_monitoring_register
525 |  | Counter | Inv [n] unit 2 DC input 1 open circuit fault | 32-bit bitfield | 24 | 1 | IREG_16001.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_1_open_circuit_fault
526 |  | Counter | Inv [n] unit 2 DC input 2 open circuit fault | 32-bit bitfield | 24 | 2 | IREG_16001.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_2_open_circuit_fault
527 |  | Counter | Inv [n] unit 2 DC input 3 open circuit fault | 32-bit bitfield | 24 | 3 | IREG_16001.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_3_open_circuit_fault
528 |  | Counter | Inv [n] unit 2 DC input 4 open circuit fault | 32-bit bitfield | 24 | 4 | IREG_16001.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_4_open_circuit_fault
529 |  | Counter | Inv [n] unit 2 DC input 5 open circuit fault | 32-bit bitfield | 24 | 5 | IREG_16001.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_5_open_circuit_fault
530 |  | Counter | Inv [n] unit 2 DC input 6 open circuit fault | 32-bit bitfield | 24 | 6 | IREG_16001.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_6_open_circuit_fault
531 |  | Counter | Inv [n] unit 2 DC input 7 open circuit fault | 32-bit bitfield | 24 | 7 | IREG_16001.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_7_open_circuit_fault
532 |  | Counter | Inv [n] unit 2 DC input 1 string failure alarm | 32-bit bitfield | 24 | 11 | IREG_16003.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_1_string_failure_alarm
533 |  | Counter | Inv [n] unit 2 DC input 2 string failure alarm | 32-bit bitfield | 24 | 12 | IREG_16003.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_2_string_failure_alarm
534 |  | Counter | Inv [n] unit 2 DC input 3 string failure alarm | 32-bit bitfield | 24 | 13 | IREG_16003.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_3_string_failure_alarm
535 |  | Counter | Inv [n] unit 2 DC input 4 string failure alarm | 32-bit bitfield | 24 | 14 | IREG_16003.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_4_string_failure_alarm
536 |  | Counter | Inv [n] unit 2 DC input 5 string failure alarm | 32-bit bitfield | 24 | 15 | IREG_16003.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_5_string_failure_alarm
537 |  | Counter | Inv [n] unit 2 DC input 6 string failure alarm | 32-bit bitfield | 24 | 16 | IREG_16003.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_6_string_failure_alarm
538 |  | Counter | Inv [n] unit 2 DC input 7 string failure alarm | 32-bit bitfield | 24 | 17 | IREG_16003.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0024_Inv_[n]_unit_2_DC_input_7_string_failure_alarm
539 | Available | Counter | Inv [n] unit 3 status register | 32-bit bitfield | 30 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0030_Inv_[n]_unit_3_status_register
540 | Available | Counter | Inv [n] unit 3 Unit is running | 32-bit bitfield | 30 | 0 | IREG_15448.17 | None | Running | Stopped | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Unit_is_running
541 | Available | Counter | Inv [n] unit 3 Unit is stopped | 32-bit bitfield | 30 | 1 | IREG_15448.18 | None | Stopped | Running | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Unit_is_stopped
542 | Available | Counter | Inv [n] unit 3 Run | 32-bit bitfield | 30 | 2 | IREG_15448.0 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Run
543 | Available | Counter | Inv [n] unit 3 Stop | 32-bit bitfield | 30 | 3 | IREG_15448.1 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Stop
544 | Available | Counter | Inv [n] unit 3 Initial standby | 32-bit bitfield | 30 | 4 | IREG_15448.2 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Initial_standby
545 | Available | Counter | Inv [n] unit 3 Press to shutdown | 32-bit bitfield | 30 | 5 | IREG_15448.3 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Press_to_shutdown
546 | Available | Counter | Inv [n] unit 3 Standby | 32-bit bitfield | 30 | 6 | IREG_15448.4 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Standby
547 | Available | Counter | Inv [n] unit 3 Emergency stop | 32-bit bitfield | 30 | 7 | IREG_15448.5 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Emergency_stop
548 | Available | Counter | Inv [n] unit 3 Starting up | 32-bit bitfield | 30 | 8 | IREG_15448.6 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Starting_up
549 | Available | Counter | Inv [n] unit 3 Shutting down | 32-bit bitfield | 30 | 9 | IREG_15448.7 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Shutting_down
550 | Available | Counter | Inv [n] unit 3 Shut down | 32-bit bitfield | 30 | 10 | IREG_15448.9 | None | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Shut_down
551 | Available | Counter | Inv [n] unit 3 Warning run | 32-bit bitfield | 30 | 11 | IREG_15448.10 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Warning_run
552 | Available | Counter | Inv [n] unit 3 Derating run | 32-bit bitfield | 30 | 12 | IREG_15448.11 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Derating_run
553 | Available | Counter | Inv [n] unit 3 IO and DSP communication error | 32-bit bitfield | 30 | 13 | IREG_15448.13 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_IO_and_DSP_communication_error
554 | Available | Counter | Inv [n] unit 3 Anti-PID run | 32-bit bitfield | 30 | 14 | IREG_15448.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Anti_PID_run
555 | Available | Counter | Inv [n] unit 3 AC breaker status | 32-bit bitfield | 30 | 15 | IREG_15434.0 | None | Closed | Open | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_AC_breaker_status
556 | Available | Counter | Inv [n] unit 3 DC switch 1 status | 32-bit bitfield | 30 | 16 | IREG_15434.3 | None | Closed | Open | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_DC_switch_1_status
557 | Available | Counter | Inv [n] unit 3 Emergency shutdown node | 32-bit bitfield | 30 | 17 | IREG_15434.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0030_Inv_[n]_unit_3_Emergency_shutdown_node
558 | Available | Counter | Inv [n] unit 3 faults register 1 | 32-bit bitfield | 31 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0031_Inv_[n]_unit_3_faults_register_1
559 | Available | Counter | Inv [n] unit 3 Smoke node | 32-bit bitfield | 31 | 0 | IREG_15434.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Smoke_node
560 | Available | Counter | Inv [n] unit 3 Access node | 32-bit bitfield | 31 | 1 | IREG_15434.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Access_node
561 | Available | Counter | Inv [n] unit 3 DC undervoltage fault | 32-bit bitfield | 31 | 2 | IREG_15426.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_undervoltage_fault
562 | Available | Counter | Inv [n] unit 3 DC overvoltage fault | 32-bit bitfield | 31 | 3 | IREG_15426.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_overvoltage_fault
563 | Available | Counter | Inv [n] unit 3 AC undervoltage fault | 32-bit bitfield | 31 | 4 | IREG_15426.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_AC_undervoltage_fault
564 | Available | Counter | Inv [n] unit 3 AC overvoltage fault | 32-bit bitfield | 31 | 5 | IREG_15426.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_AC_overvoltage_fault
565 | Available | Counter | Inv [n] unit 3 Anti islanding protection active | 32-bit bitfield | 31 | 6 | IREG_15426.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Anti_islanding_protection_active
566 | Available | Counter | Inv [n] unit 3 PDP protection active | 32-bit bitfield | 31 | 7 | IREG_15426.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_PDP_protection_active
567 | Available | Counter | Inv [n] unit 3 Module overtemperature fault | 32-bit bitfield | 31 | 8 | IREG_15426.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Module_overtemperature_fault
568 | Available | Counter | Inv [n] unit 3 Reactor overtemperature fault | 32-bit bitfield | 31 | 9 | IREG_15426.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Reactor_overtemperature_fault
569 | Available | Counter | Inv [n] unit 3 AC leakage current protection fault | 32-bit bitfield | 31 | 10 | IREG_15426.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_AC_leakage_current_protection_fault
570 | Available | Counter | Inv [n] unit 3 GFDI protection active | 32-bit bitfield | 31 | 11 | IREG_15426.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_GFDI_protection_active
571 | Available | Counter | Inv [n] unit 3 Fan 1 fault | 32-bit bitfield | 31 | 12 | IREG_15426.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Fan_1_fault
572 | Available | Counter | Inv [n] unit 3 DC overcurrent | 32-bit bitfield | 31 | 13 | IREG_15426.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_overcurrent
573 | Available | Counter | Inv [n] unit 3 AC overcurrent | 32-bit bitfield | 31 | 14 | IREG_15426.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_AC_overcurrent
574 | Available | Counter | Inv [n] unit 3 Frequency abnormal | 32-bit bitfield | 31 | 15 | IREG_15426.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Frequency_abnormal
575 | Available | Counter | Inv [n] unit 3 Temperature abnormal | 32-bit bitfield | 31 | 16 | IREG_15426.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Temperature_abnormal
576 | Available | Counter | Inv [n] unit 3 Hardware fault | 32-bit bitfield | 31 | 17 | IREG_15426.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Hardware_fault
577 | Available | Counter | Inv [n] unit 3 Grounding fault | 32-bit bitfield | 31 | 18 | IREG_15426.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Grounding_fault
578 | Available | Counter | Inv [n] unit 3 Bus overvoltage | 32-bit bitfield | 31 | 19 | IREG_15426.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Bus_overvoltage
579 | Available | Counter | Inv [n] unit 3 Bus undervoltage | 32-bit bitfield | 31 | 20 | IREG_15426.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Bus_undervoltage
580 | Available | Counter | Inv [n] unit 3 Inverter overvoltage | 32-bit bitfield | 31 | 21 | IREG_15426.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Inverter_overvoltage
581 | Available | Counter | Inv [n] unit 3 Low insulation resistance fault | 32-bit bitfield | 31 | 22 | IREG_15428.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Low_insulation_resistance_fault
582 | Available | Counter | Inv [n] unit 3 AC SPD fault | 32-bit bitfield | 31 | 23 | IREG_15428.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_AC_SPD_fault
583 | Available | Counter | Inv [n] unit 3 Sampling fault | 32-bit bitfield | 31 | 24 | IREG_15428.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Sampling_fault
584 | Available | Counter | Inv [n] unit 3 DC polarity reversed fault | 32-bit bitfield | 31 | 25 | IREG_15428.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_polarity_reversed_fault
585 | Available | Counter | Inv [n] unit 3 Control power supply fault | 32-bit bitfield | 31 | 26 | IREG_15428.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Control_power_supply_fault
586 | Available | Counter | Inv [n] unit 3 AC current imballance | 32-bit bitfield | 31 | 27 | IREG_15428.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_AC_current_imballance
587 | Available | Counter | Inv [n] unit 3 DC SPD fault | 32-bit bitfield | 31 | 28 | IREG_15428.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_SPD_fault
588 | Available | Counter | Inv [n] unit 3 DC component fault | 32-bit bitfield | 31 | 29 | IREG_15428.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_component_fault
589 | Available | Counter | Inv [n] unit 3 DC switch fault | 32-bit bitfield | 31 | 30 | IREG_15428.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_DC_switch_fault
590 | Available | Counter | Inv [n] unit 3 Repeated fault | 32-bit bitfield | 31 | 31 | IREG_15428.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0031_Inv_[n]_unit_3_Repeated_fault
591 | Available | Counter | Inv [n] unit 3 faults register 2 | 32-bit bitfield | 32 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0032_Inv_[n]_unit_3_faults_register_2
592 | Available | Counter | Inv [n] unit 3 Parallel operation communication failure | 32-bit bitfield | 32 | 0 | IREG_15428.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Parallel_operation_communication_failure
593 | Available | Counter | Inv [n] unit 3 Control cabinet temperature fault | 32-bit bitfield | 32 | 1 | IREG_15428.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Control_cabinet_temperature_fault
594 | Available | Counter | Inv [n] unit 3 DC fuse ground fault | 32-bit bitfield | 32 | 2 | IREG_15428.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_DC_fuse_ground_fault
595 | Available | Counter | Inv [n] unit 3 Excessive DC reverse current fault | 32-bit bitfield | 32 | 3 | IREG_15428.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Excessive_DC_reverse_current_fault
596 | Available | Counter | Inv [n] unit 3 Grid voltage imballance fault | 32-bit bitfield | 32 | 4 | IREG_15428.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Grid_voltage_imballance_fault
597 | Available | Counter | Inv [n] unit 3 Inverter cabinet temperature fault | 32-bit bitfield | 32 | 5 | IREG_15428.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Inverter_cabinet_temperature_fault
598 | Available | Counter | Inv [n] unit 3 AC cabinet temperature fault | 32-bit bitfield | 32 | 6 | IREG_15428.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_AC_cabinet_temperature_fault
599 | Available | Counter | Inv [n] unit 3 AC switch off | 32-bit bitfield | 32 | 7 | IREG_15428.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_AC_switch_off
600 | Available | Counter | Inv [n] unit 3 AC switch fault | 32-bit bitfield | 32 | 8 | IREG_15428.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_AC_switch_fault
601 | Available | Counter | Inv [n] unit 3 Soft start fault | 32-bit bitfield | 32 | 9 | IREG_15428.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Soft_start_fault
602 | Available | Counter | Inv [n] unit 3 DC voltage sampling fault | 32-bit bitfield | 32 | 10 | IREG_15428.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_DC_voltage_sampling_fault
603 | Available | Counter | Inv [n] unit 3 Fan 2 fault | 32-bit bitfield | 32 | 11 | IREG_15428.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Fan_2_fault
604 | Available | Counter | Inv [n] unit 3 Current unbalance 2 | 32-bit bitfield | 32 | 12 | IREG_15428.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Current_unbalance_2
605 | Available | Counter | Inv [n] unit 3 Current unbalance 3 | 32-bit bitfield | 32 | 13 | IREG_15428.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Current_unbalance_3
606 | Available | Counter | Inv [n] unit 3 DC cabinet temperature alarm | 32-bit bitfield | 32 | 14 | IREG_15428.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_DC_cabinet_temperature_alarm
607 | Available | Counter | Inv [n] unit 3 Neutral point potential shift alarm | 32-bit bitfield | 32 | 15 | IREG_15428.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Neutral_point_potential_shift_alarm
608 | Available | Counter | Inv [n] unit 3 Carrier sync failure | 32-bit bitfield | 32 | 16 | IREG_15428.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Carrier_sync_failure
609 | Available | Counter | Inv [n] unit 3 Smoke alarm | 32-bit bitfield | 32 | 17 | IREG_15430.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Smoke_alarm
610 | Available | Counter | Inv [n] unit 3 Access control protection alarm | 32-bit bitfield | 32 | 18 | IREG_15430.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Access_control_protection_alarm
611 | Available | Counter | Inv [n] unit 3 Emergency shutdown alarm | 32-bit bitfield | 32 | 19 | IREG_15430.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0032_Inv_[n]_unit_3_Emergency_shutdown_alarm
612 | Available | Counter | Inv [n] unit 3 alarms register | 32-bit bitfield | 33 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0033_Inv_[n]_unit_3_alarms_register
613 | Available | Counter | Inv [n] unit 3 Temperature abnormal alarm | 32-bit bitfield | 33 | 0 | IREG_15450.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Temperature_abnormal_alarm
614 | Available | Counter | Inv [n] unit 3 Low insulation resistance alarm | 32-bit bitfield | 33 | 1 | IREG_15450.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Low_insulation_resistance_alarm
615 | Available | Counter | Inv [n] unit 3 GFRT operation alarm | 32-bit bitfield | 33 | 2 | IREG_15450.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_GFRT_operation_alarm
616 | Available | Counter | Inv [n] unit 3 CT unbalance alarm | 32-bit bitfield | 33 | 3 | IREG_15450.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_CT_unbalance_alarm
617 | Available | Counter | Inv [n] unit 3 DC sensor alarm | 32-bit bitfield | 33 | 4 | IREG_15450.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_DC_sensor_alarm
618 | Available | Counter | Inv [n] unit 3 DC SPD alarm | 32-bit bitfield | 33 | 5 | IREG_15450.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_DC_SPD_alarm
619 | Available | Counter | Inv [n] unit 3 AC SPD alarm | 32-bit bitfield | 33 | 6 | IREG_15450.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_AC_SPD_alarm
620 | Available | Counter | Inv [n] unit 3 DC switch alarm | 32-bit bitfield | 33 | 7 | IREG_15450.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_DC_switch_alarm
621 | Available | Counter | Inv [n] unit 3 Anti-PID power alarm | 32-bit bitfield | 33 | 8 | IREG_15450.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Anti_PID_power_alarm
622 | Available | Counter | Inv [n] unit 3 Cooling fan 1 alarm | 32-bit bitfield | 33 | 9 | IREG_15450.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Cooling_fan_1_alarm
623 | Available | Counter | Inv [n] unit 3 DC branch forward alarm | 32-bit bitfield | 33 | 10 | IREG_15450.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_DC_branch_forward_alarm
624 | Available | Counter | Inv [n] unit 3 DC branch reverse alarm | 32-bit bitfield | 33 | 11 | IREG_15450.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_DC_branch_reverse_alarm
625 | Available | Counter | Inv [n] unit 3 AC switch alarm | 32-bit bitfield | 33 | 12 | IREG_15450.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_AC_switch_alarm
626 | Available | Counter | Inv [n] unit 3 Meter communication failure alarm | 32-bit bitfield | 33 | 13 | IREG_15450.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Meter_communication_failure_alarm
627 | Available | Counter | Inv [n] unit 3 Cooling fan 2 alarm | 32-bit bitfield | 33 | 14 | IREG_15450.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Cooling_fan_2_alarm
628 | Available | Counter | Inv [n] unit 3 Temperature and humidity sensor alarm | 32-bit bitfield | 33 | 15 | IREG_15450.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Temperature_and_humidity_sensor_alarm
629 | Available | Counter | Inv [n] unit 3 Frequency deviation active power regulation | 32-bit bitfield | 33 | 16 | IREG_15450.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Frequency_deviation_active_power_regulation
630 | Available | Counter | Inv [n] unit 3 Voltage deviation reactive power regulation | 32-bit bitfield | 33 | 17 | IREG_15450.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Voltage_deviation_reactive_power_regulation
631 | Available | Counter | Inv [n] unit 3 Busbar temperature alarm | 32-bit bitfield | 33 | 18 | IREG_15450.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Busbar_temperature_alarm
632 | Available | Counter | Inv [n] unit 3 Cooling fan derating alarm | 32-bit bitfield | 33 | 19 | IREG_15450.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Cooling_fan_derating_alarm
633 | Available | Counter | Inv [n] unit 3 Frequency abnormal | 32-bit bitfield | 33 | 20 | IREG_15450.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_Frequency_abnormal
634 | Available | Counter | Inv [n] unit 3 HVRT operation | 32-bit bitfield | 33 | 21 | IREG_15502.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_HVRT_operation
635 | Available | Counter | Inv [n] unit 3 LVRT operation | 32-bit bitfield | 33 | 22 | IREG_15502.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0033_Inv_[n]_unit_3_LVRT_operation
636 |  | Counter | Inv [n] unit 3 array monitoring register | 32-bit bitfield | 34 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0034_Inv_[n]_unit_3_array_monitoring_register
637 |  | Counter | Inv [n] unit 3 DC input 1 open circuit fault | 32-bit bitfield | 34 | 1 | IREG_16001.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_1_open_circuit_fault
638 |  | Counter | Inv [n] unit 3 DC input 2 open circuit fault | 32-bit bitfield | 34 | 2 | IREG_16001.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_2_open_circuit_fault
639 |  | Counter | Inv [n] unit 3 DC input 3 open circuit fault | 32-bit bitfield | 34 | 3 | IREG_16001.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_3_open_circuit_fault
640 |  | Counter | Inv [n] unit 3 DC input 4 open circuit fault | 32-bit bitfield | 34 | 4 | IREG_16001.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_4_open_circuit_fault
641 |  | Counter | Inv [n] unit 3 DC input 5 open circuit fault | 32-bit bitfield | 34 | 5 | IREG_16001.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_5_open_circuit_fault
642 |  | Counter | Inv [n] unit 3 DC input 6 open circuit fault | 32-bit bitfield | 34 | 6 | IREG_16001.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_6_open_circuit_fault
643 |  | Counter | Inv [n] unit 3 DC input 7 open circuit fault | 32-bit bitfield | 34 | 7 | IREG_16001.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_7_open_circuit_fault
644 |  | Counter | Inv [n] unit 3 DC input 1 string failure alarm | 32-bit bitfield | 34 | 11 | IREG_16003.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_1_string_failure_alarm
645 |  | Counter | Inv [n] unit 3 DC input 2 string failure alarm | 32-bit bitfield | 34 | 12 | IREG_16003.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_2_string_failure_alarm
646 |  | Counter | Inv [n] unit 3 DC input 3 string failure alarm | 32-bit bitfield | 34 | 13 | IREG_16003.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_3_string_failure_alarm
647 |  | Counter | Inv [n] unit 3 DC input 4 string failure alarm | 32-bit bitfield | 34 | 14 | IREG_16003.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_4_string_failure_alarm
648 |  | Counter | Inv [n] unit 3 DC input 5 string failure alarm | 32-bit bitfield | 34 | 15 | IREG_16003.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_5_string_failure_alarm
649 |  | Counter | Inv [n] unit 3 DC input 6 string failure alarm | 32-bit bitfield | 34 | 16 | IREG_16003.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_6_string_failure_alarm
650 |  | Counter | Inv [n] unit 3 DC input 7 string failure alarm | 32-bit bitfield | 34 | 17 | IREG_16003.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0034_Inv_[n]_unit_3_DC_input_7_string_failure_alarm
651 | Available | Counter | Inv [n] unit 4 status register | 32-bit bitfield | 40 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0040_Inv_[n]_unit_4_status_register
652 | Available | Counter | Inv [n] unit 4 Unit is running | 32-bit bitfield | 40 | 0 | IREG_15568.17 | None | Running | Stopped | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Unit_is_running
653 | Available | Counter | Inv [n] unit 4 Unit is stopped | 32-bit bitfield | 40 | 1 | IREG_15568.18 | None | Stopped | Running | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Unit_is_stopped
654 | Available | Counter | Inv [n] unit 4 Run | 32-bit bitfield | 40 | 2 | IREG_15568.0 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Run
655 | Available | Counter | Inv [n] unit 4 Stop | 32-bit bitfield | 40 | 3 | IREG_15568.1 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Stop
656 | Available | Counter | Inv [n] unit 4 Initial standby | 32-bit bitfield | 40 | 4 | IREG_15568.2 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Initial_standby
657 | Available | Counter | Inv [n] unit 4 Press to shutdown | 32-bit bitfield | 40 | 5 | IREG_15568.3 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Press_to_shutdown
658 | Available | Counter | Inv [n] unit 4 Standby | 32-bit bitfield | 40 | 6 | IREG_15568.4 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Standby
659 | Available | Counter | Inv [n] unit 4 Emergency stop | 32-bit bitfield | 40 | 7 | IREG_15568.5 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Emergency_stop
660 | Available | Counter | Inv [n] unit 4 Starting up | 32-bit bitfield | 40 | 8 | IREG_15568.6 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Starting_up
661 | Available | Counter | Inv [n] unit 4 Shutting down | 32-bit bitfield | 40 | 9 | IREG_15568.7 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Shutting_down
662 | Available | Counter | Inv [n] unit 4 Shut down | 32-bit bitfield | 40 | 10 | IREG_15568.9 | None | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Shut_down
663 | Available | Counter | Inv [n] unit 4 Warning run | 32-bit bitfield | 40 | 11 | IREG_15568.10 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Warning_run
664 | Available | Counter | Inv [n] unit 4 Derating run | 32-bit bitfield | 40 | 12 | IREG_15568.11 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Derating_run
665 | Available | Counter | Inv [n] unit 4 IO and DSP communication error | 32-bit bitfield | 40 | 13 | IREG_15568.13 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_IO_and_DSP_communication_error
666 | Available | Counter | Inv [n] unit 4 Anti-PID run | 32-bit bitfield | 40 | 14 | IREG_15568.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Anti_PID_run
667 | Available | Counter | Inv [n] unit 4 AC breaker status | 32-bit bitfield | 40 | 15 | IREG_15554.0 | None | Closed | Open | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_AC_breaker_status
668 | Available | Counter | Inv [n] unit 4 DC switch 1 status | 32-bit bitfield | 40 | 16 | IREG_15554.3 | None | Closed | Open | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_DC_switch_1_status
669 | Available | Counter | Inv [n] unit 4 Emergency shutdown node | 32-bit bitfield | 40 | 17 | IREG_15554.19 | On (1) | On | Off | [8 empty] | Change events |  | CNT_0040_Inv_[n]_unit_4_Emergency_shutdown_node
670 | Available | Counter | Inv [n] unit 4 faults register 1 | 32-bit bitfield | 41 |  | PPC Logic | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0041_Inv_[n]_unit_4_faults_register_1
671 | Available | Counter | Inv [n] unit 4 Smoke node | 32-bit bitfield | 41 | 0 | IREG_15554.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Smoke_node
672 | Available | Counter | Inv [n] unit 4 Access node | 32-bit bitfield | 41 | 1 | IREG_15554.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Access_node
673 | Available | Counter | Inv [n] unit 4 DC undervoltage fault | 32-bit bitfield | 41 | 2 | IREG_15546.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_undervoltage_fault
674 | Available | Counter | Inv [n] unit 4 DC overvoltage fault | 32-bit bitfield | 41 | 3 | IREG_15546.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_overvoltage_fault
675 | Available | Counter | Inv [n] unit 4 AC undervoltage fault | 32-bit bitfield | 41 | 4 | IREG_15546.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_AC_undervoltage_fault
676 | Available | Counter | Inv [n] unit 4 AC overvoltage fault | 32-bit bitfield | 41 | 5 | IREG_15546.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_AC_overvoltage_fault
677 | Available | Counter | Inv [n] unit 4 Anti islanding protection active | 32-bit bitfield | 41 | 6 | IREG_15546.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Anti_islanding_protection_active
678 | Available | Counter | Inv [n] unit 4 PDP protection active | 32-bit bitfield | 41 | 7 | IREG_15546.9 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_PDP_protection_active
679 | Available | Counter | Inv [n] unit 4 Module overtemperature fault | 32-bit bitfield | 41 | 8 | IREG_15546.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Module_overtemperature_fault
680 | Available | Counter | Inv [n] unit 4 Reactor overtemperature fault | 32-bit bitfield | 41 | 9 | IREG_15546.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Reactor_overtemperature_fault
681 | Available | Counter | Inv [n] unit 4 AC leakage current protection fault | 32-bit bitfield | 41 | 10 | IREG_15546.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_AC_leakage_current_protection_fault
682 | Available | Counter | Inv [n] unit 4 GFDI protection active | 32-bit bitfield | 41 | 11 | IREG_15546.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_GFDI_protection_active
683 | Available | Counter | Inv [n] unit 4 Fan 1 fault | 32-bit bitfield | 41 | 12 | IREG_15546.18 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Fan_1_fault
684 | Available | Counter | Inv [n] unit 4 DC overcurrent | 32-bit bitfield | 41 | 13 | IREG_15546.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_overcurrent
685 | Available | Counter | Inv [n] unit 4 AC overcurrent | 32-bit bitfield | 41 | 14 | IREG_15546.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_AC_overcurrent
686 | Available | Counter | Inv [n] unit 4 Frequency abnormal | 32-bit bitfield | 41 | 15 | IREG_15546.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Frequency_abnormal
687 | Available | Counter | Inv [n] unit 4 Temperature abnormal | 32-bit bitfield | 41 | 16 | IREG_15546.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Temperature_abnormal
688 | Available | Counter | Inv [n] unit 4 Hardware fault | 32-bit bitfield | 41 | 17 | IREG_15546.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Hardware_fault
689 | Available | Counter | Inv [n] unit 4 Grounding fault | 32-bit bitfield | 41 | 18 | IREG_15546.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Grounding_fault
690 | Available | Counter | Inv [n] unit 4 Bus overvoltage | 32-bit bitfield | 41 | 19 | IREG_15546.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Bus_overvoltage
691 | Available | Counter | Inv [n] unit 4 Bus undervoltage | 32-bit bitfield | 41 | 20 | IREG_15546.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Bus_undervoltage
692 | Available | Counter | Inv [n] unit 4 Inverter overvoltage | 32-bit bitfield | 41 | 21 | IREG_15546.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Inverter_overvoltage
693 | Available | Counter | Inv [n] unit 4 Low insulation resistance fault | 32-bit bitfield | 41 | 22 | IREG_15548.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Low_insulation_resistance_fault
694 | Available | Counter | Inv [n] unit 4 AC SPD fault | 32-bit bitfield | 41 | 23 | IREG_15548.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_AC_SPD_fault
695 | Available | Counter | Inv [n] unit 4 Sampling fault | 32-bit bitfield | 41 | 24 | IREG_15548.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Sampling_fault
696 | Available | Counter | Inv [n] unit 4 DC polarity reversed fault | 32-bit bitfield | 41 | 25 | IREG_15548.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_polarity_reversed_fault
697 | Available | Counter | Inv [n] unit 4 Control power supply fault | 32-bit bitfield | 41 | 26 | IREG_15548.4 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Control_power_supply_fault
698 | Available | Counter | Inv [n] unit 4 AC current imballance | 32-bit bitfield | 41 | 27 | IREG_15548.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_AC_current_imballance
699 | Available | Counter | Inv [n] unit 4 DC SPD fault | 32-bit bitfield | 41 | 28 | IREG_15548.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_SPD_fault
700 | Available | Counter | Inv [n] unit 4 DC component fault | 32-bit bitfield | 41 | 29 | IREG_15548.10 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_component_fault
701 | Available | Counter | Inv [n] unit 4 DC switch fault | 32-bit bitfield | 41 | 30 | IREG_15548.11 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_DC_switch_fault
702 | Available | Counter | Inv [n] unit 4 Repeated fault | 32-bit bitfield | 41 | 31 | IREG_15548.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0041_Inv_[n]_unit_4_Repeated_fault
703 | Available | Counter | Inv [n] unit 4 faults register 2 | 32-bit bitfield | 42 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0042_Inv_[n]_unit_4_faults_register_2
704 | Available | Counter | Inv [n] unit 4 Parallel operation communication failure | 32-bit bitfield | 42 | 0 | IREG_15548.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Parallel_operation_communication_failure
705 | Available | Counter | Inv [n] unit 4 Control cabinet temperature fault | 32-bit bitfield | 42 | 1 | IREG_15548.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Control_cabinet_temperature_fault
706 | Available | Counter | Inv [n] unit 4 DC fuse ground fault | 32-bit bitfield | 42 | 2 | IREG_15548.15 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_DC_fuse_ground_fault
707 | Available | Counter | Inv [n] unit 4 Excessive DC reverse current fault | 32-bit bitfield | 42 | 3 | IREG_15548.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Excessive_DC_reverse_current_fault
708 | Available | Counter | Inv [n] unit 4 Grid voltage imballance fault | 32-bit bitfield | 42 | 4 | IREG_15548.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Grid_voltage_imballance_fault
709 | Available | Counter | Inv [n] unit 4 Inverter cabinet temperature fault | 32-bit bitfield | 42 | 5 | IREG_15548.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Inverter_cabinet_temperature_fault
710 | Available | Counter | Inv [n] unit 4 AC cabinet temperature fault | 32-bit bitfield | 42 | 6 | IREG_15548.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_AC_cabinet_temperature_fault
711 | Available | Counter | Inv [n] unit 4 AC switch off | 32-bit bitfield | 42 | 7 | IREG_15548.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_AC_switch_off
712 | Available | Counter | Inv [n] unit 4 AC switch fault | 32-bit bitfield | 42 | 8 | IREG_15548.22 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_AC_switch_fault
713 | Available | Counter | Inv [n] unit 4 Soft start fault | 32-bit bitfield | 42 | 9 | IREG_15548.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Soft_start_fault
714 | Available | Counter | Inv [n] unit 4 DC voltage sampling fault | 32-bit bitfield | 42 | 10 | IREG_15548.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_DC_voltage_sampling_fault
715 | Available | Counter | Inv [n] unit 4 Fan 2 fault | 32-bit bitfield | 42 | 11 | IREG_15548.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Fan_2_fault
716 | Available | Counter | Inv [n] unit 4 Current unbalance 2 | 32-bit bitfield | 42 | 12 | IREG_15548.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Current_unbalance_2
717 | Available | Counter | Inv [n] unit 4 Current unbalance 3 | 32-bit bitfield | 42 | 13 | IREG_15548.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Current_unbalance_3
718 | Available | Counter | Inv [n] unit 4 DC cabinet temperature alarm | 32-bit bitfield | 42 | 14 | IREG_15548.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_DC_cabinet_temperature_alarm
719 | Available | Counter | Inv [n] unit 4 Neutral point potential shift alarm | 32-bit bitfield | 42 | 15 | IREG_15548.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Neutral_point_potential_shift_alarm
720 | Available | Counter | Inv [n] unit 4 Carrier sync failure | 32-bit bitfield | 42 | 16 | IREG_15548.31 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Carrier_sync_failure
721 | Available | Counter | Inv [n] unit 4 Smoke alarm | 32-bit bitfield | 42 | 17 | IREG_15550.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Smoke_alarm
722 | Available | Counter | Inv [n] unit 4 Access control protection alarm | 32-bit bitfield | 42 | 18 | IREG_15550.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Access_control_protection_alarm
723 | Available | Counter | Inv [n] unit 4 Emergency shutdown alarm | 32-bit bitfield | 42 | 19 | IREG_15550.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0042_Inv_[n]_unit_4_Emergency_shutdown_alarm
724 | Available | Counter | Inv [n] unit 4 alarms register | 32-bit bitfield | 43 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0043_Inv_[n]_unit_4_alarms_register
725 | Available | Counter | Inv [n] unit 4 Temperature abnormal alarm | 32-bit bitfield | 43 | 0 | IREG_15570.0 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Temperature_abnormal_alarm
726 | Available | Counter | Inv [n] unit 4 Low insulation resistance alarm | 32-bit bitfield | 43 | 1 | IREG_15570.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Low_insulation_resistance_alarm
727 | Available | Counter | Inv [n] unit 4 GFRT operation alarm | 32-bit bitfield | 43 | 2 | IREG_15570.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_GFRT_operation_alarm
728 | Available | Counter | Inv [n] unit 4 CT unbalance alarm | 32-bit bitfield | 43 | 3 | IREG_15570.3 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_CT_unbalance_alarm
729 | Available | Counter | Inv [n] unit 4 DC sensor alarm | 32-bit bitfield | 43 | 4 | IREG_15570.6 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_DC_sensor_alarm
730 | Available | Counter | Inv [n] unit 4 DC SPD alarm | 32-bit bitfield | 43 | 5 | IREG_15570.7 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_DC_SPD_alarm
731 | Available | Counter | Inv [n] unit 4 AC SPD alarm | 32-bit bitfield | 43 | 6 | IREG_15570.8 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_AC_SPD_alarm
732 | Available | Counter | Inv [n] unit 4 DC switch alarm | 32-bit bitfield | 43 | 7 | IREG_15570.12 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_DC_switch_alarm
733 | Available | Counter | Inv [n] unit 4 Anti-PID power alarm | 32-bit bitfield | 43 | 8 | IREG_15570.13 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Anti_PID_power_alarm
734 | Available | Counter | Inv [n] unit 4 Cooling fan 1 alarm | 32-bit bitfield | 43 | 9 | IREG_15570.14 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Cooling_fan_1_alarm
735 | Available | Counter | Inv [n] unit 4 DC branch forward alarm | 32-bit bitfield | 43 | 10 | IREG_15570.16 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_DC_branch_forward_alarm
736 | Available | Counter | Inv [n] unit 4 DC branch reverse alarm | 32-bit bitfield | 43 | 11 | IREG_15570.17 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_DC_branch_reverse_alarm
737 | Available | Counter | Inv [n] unit 4 AC switch alarm | 32-bit bitfield | 43 | 12 | IREG_15570.19 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_AC_switch_alarm
738 | Available | Counter | Inv [n] unit 4 Meter communication failure alarm | 32-bit bitfield | 43 | 13 | IREG_15570.20 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Meter_communication_failure_alarm
739 | Available | Counter | Inv [n] unit 4 Cooling fan 2 alarm | 32-bit bitfield | 43 | 14 | IREG_15570.21 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Cooling_fan_2_alarm
740 | Available | Counter | Inv [n] unit 4 Temperature and humidity sensor alarm | 32-bit bitfield | 43 | 15 | IREG_15570.23 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Temperature_and_humidity_sensor_alarm
741 | Available | Counter | Inv [n] unit 4 Frequency deviation active power regulation | 32-bit bitfield | 43 | 16 | IREG_15570.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Frequency_deviation_active_power_regulation
742 | Available | Counter | Inv [n] unit 4 Voltage deviation reactive power regulation | 32-bit bitfield | 43 | 17 | IREG_15570.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Voltage_deviation_reactive_power_regulation
743 | Available | Counter | Inv [n] unit 4 Busbar temperature alarm | 32-bit bitfield | 43 | 18 | IREG_15570.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Busbar_temperature_alarm
744 | Available | Counter | Inv [n] unit 4 Cooling fan derating alarm | 32-bit bitfield | 43 | 19 | IREG_15570.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Cooling_fan_derating_alarm
745 | Available | Counter | Inv [n] unit 4 Frequency abnormal | 32-bit bitfield | 43 | 20 | IREG_15570.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_Frequency_abnormal
746 | Available | Counter | Inv [n] unit 4 HVRT operation | 32-bit bitfield | 43 | 21 | IREG_15622.1 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_HVRT_operation
747 | Available | Counter | Inv [n] unit 4 LVRT operation | 32-bit bitfield | 43 | 22 | IREG_15622.2 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0043_Inv_[n]_unit_4_LVRT_operation
748 |  | Counter | Inv [n] unit 4 array monitoring register | 32-bit bitfield | 44 |  |  | None |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0044_Inv_[n]_unit_4_array_monitoring_register
749 |  | Counter | Inv [n] unit 4 DC input 1 open circuit fault | 32-bit bitfield | 44 | 1 | IREG_16001.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_1_open_circuit_fault
750 |  | Counter | Inv [n] unit 4 DC input 2 open circuit fault | 32-bit bitfield | 44 | 2 | IREG_16001.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_2_open_circuit_fault
751 |  | Counter | Inv [n] unit 4 DC input 3 open circuit fault | 32-bit bitfield | 44 | 3 | IREG_16001.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_3_open_circuit_fault
752 |  | Counter | Inv [n] unit 4 DC input 4 open circuit fault | 32-bit bitfield | 44 | 4 | IREG_16001.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_4_open_circuit_fault
753 |  | Counter | Inv [n] unit 4 DC input 5 open circuit fault | 32-bit bitfield | 44 | 5 | IREG_16001.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_5_open_circuit_fault
754 |  | Counter | Inv [n] unit 4 DC input 6 open circuit fault | 32-bit bitfield | 44 | 6 | IREG_16001.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_6_open_circuit_fault
755 |  | Counter | Inv [n] unit 4 DC input 7 open circuit fault | 32-bit bitfield | 44 | 7 | IREG_16001.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_7_open_circuit_fault
756 |  | Counter | Inv [n] unit 4 DC input 1 string failure alarm | 32-bit bitfield | 44 | 11 | IREG_16003.24 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_1_string_failure_alarm
757 |  | Counter | Inv [n] unit 4 DC input 2 string failure alarm | 32-bit bitfield | 44 | 12 | IREG_16003.25 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_2_string_failure_alarm
758 |  | Counter | Inv [n] unit 4 DC input 3 string failure alarm | 32-bit bitfield | 44 | 13 | IREG_16003.26 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_3_string_failure_alarm
759 |  | Counter | Inv [n] unit 4 DC input 4 string failure alarm | 32-bit bitfield | 44 | 14 | IREG_16003.27 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_4_string_failure_alarm
760 |  | Counter | Inv [n] unit 4 DC input 5 string failure alarm | 32-bit bitfield | 44 | 15 | IREG_16003.28 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_5_string_failure_alarm
761 |  | Counter | Inv [n] unit 4 DC input 6 string failure alarm | 32-bit bitfield | 44 | 16 | IREG_16003.29 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_6_string_failure_alarm
762 |  | Counter | Inv [n] unit 4 DC input 7 string failure alarm | 32-bit bitfield | 44 | 17 | IREG_16003.30 | On (1) | Alarm | Normal | [8 empty] | Change events | Alarms | CNT_0044_Inv_[n]_unit_4_DC_input_7_string_failure_alarm
763 | Available | Counter | Inv [n] MV node status register (transformer) | 32-bit bitfield | 100 |  | IREG_15114 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0100_Inv_[n]_MV_node_status_register_(transformer)
764 | Available | Counter | Inv [n] Entire system working state register | 32-bit bitfield | 101 |  | IREG_15117 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0101_Inv_[n]_Entire_system_working_state_register
765 | Available | Counter | Inv [n] MV node status 1 register | 32-bit bitfield | 102 |  | IREG_15126 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0102_Inv_[n]_MV_node_status_1_register
766 | Available | Counter | Inv [n] MV node status 2 register | 32-bit bitfield | 103 |  | IREG_15131 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0103_Inv_[n]_MV_node_status_2_register
767 | Available | Counter | Inv [n] Overall alarm status register | 32-bit bitfield | 104 |  | IREG_15127 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0104_Inv_[n]_Overall_alarm_status_register
768 | Available | Counter | Inv [n] DI node status register | 32-bit bitfield | 105 |  | IREG_15129 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0105_Inv_[n]_DI_node_status_register
769 | Available | Counter | Inv [n] PMD_IODI input status register | 32-bit bitfield | 106 |  | IREG_15142 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0106_Inv_[n]_PMD_IODI_input_status_register
770 | Available | Counter | Inv [n] UPS conversion status register | 32-bit bitfield | 107 |  | IREG_15146 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0107_Inv_[n]_UPS_conversion_status_register
771 | Available | Counter | Inv [n] UPS alarm status regsiter | 32-bit bitfield | 108 |  | IREG_15147 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0108_Inv_[n]_UPS_alarm_status_regsiter
772 | Available | Counter | Inv [n] ISO board fault status register | 32-bit bitfield | 109 |  | IREG_15630 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0109_Inv_[n]_ISO_board_fault_status_register
773 | Available | Counter | Inv [n] ISO board alarm status register | 32-bit bitfield | 110 |  | IREG_15631 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0110_Inv_[n]_ISO_board_alarm_status_register
774 | Available | Counter | Inv [n] Branch open circuit alarm register | 32-bit bitfield | 111 |  | IREG_16001 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0111_Inv_[n]_Branch_open_circuit_alarm_register
775 | Available | Counter | Inv [n] Branch string fault alarm register | 32-bit bitfield | 112 |  | IREG_16003 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0112_Inv_[n]_Branch_string_fault_alarm_register
776 | Available | Counter | Inv [n] unit 1 fault status 1 register | 32-bit bitfield | 113 |  | IREG_15186 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0113_Inv_[n]_unit_1_fault_status_1_register
777 | Available | Counter | Inv [n] unit 1 fault status 2 register | 32-bit bitfield | 114 |  | IREG_15188 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0114_Inv_[n]_unit_1_fault_status_2_register
778 | Available | Counter | Inv [n] unit 1 fault status 3 register | 32-bit bitfield | 115 |  | IREG_15190 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0115_Inv_[n]_unit_1_fault_status_3_register
779 | Available | Counter | Inv [n] unit 1 node status register | 32-bit bitfield | 116 |  | IREG_15194 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0116_Inv_[n]_unit_1_node_status_register
780 |  | Counter | Inv [n] unit 1 working status register | 32-bit bitfield | 117 |  | IREG_15208 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0117_Inv_[n]_unit_1_working_status_register
781 |  | Counter | Inv [n] unit 1 alarm status register | 32-bit bitfield | 118 |  | IREG_15210 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0118_Inv_[n]_unit_1_alarm_status_register
782 |  | Counter | Inv [n] unit 1 running status register | 32-bit bitfield | 119 |  | IREG_15262 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0119_Inv_[n]_unit_1_running_status_register
783 |  | Counter | Inv [n] unit 2 fault status 1 register | 32-bit bitfield | 120 |  | IREG_15306 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0120_Inv_[n]_unit_2_fault_status_1_register
784 |  | Counter | Inv [n] unit 2 fault status 2 register | 32-bit bitfield | 121 |  | IREG_15308 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0121_Inv_[n]_unit_2_fault_status_2_register
785 |  | Counter | Inv [n] unit 2 fault status 3 register | 32-bit bitfield | 122 |  | IREG_15310 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0122_Inv_[n]_unit_2_fault_status_3_register
786 |  | Counter | Inv [n] unit 2 node status register | 32-bit bitfield | 123 |  | IREG_15314 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0123_Inv_[n]_unit_2_node_status_register
787 |  | Counter | Inv [n] unit 2 working status register | 32-bit bitfield | 124 |  | IREG_15328 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0124_Inv_[n]_unit_2_working_status_register
788 |  | Counter | Inv [n] unit 2 alarm status register | 32-bit bitfield | 125 |  | IREG_15330 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0125_Inv_[n]_unit_2_alarm_status_register
789 |  | Counter | Inv [n] unit 2 running status register | 32-bit bitfield | 126 |  | IREG_15382 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0126_Inv_[n]_unit_2_running_status_register
790 |  | Counter | Inv [n] unit 3 fault status 1 register | 32-bit bitfield | 127 |  | IREG_15426 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0127_Inv_[n]_unit_3_fault_status_1_register
791 |  | Counter | Inv [n] unit 3 fault status 2 register | 32-bit bitfield | 128 |  | IREG_15428 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0128_Inv_[n]_unit_3_fault_status_2_register
792 |  | Counter | Inv [n] unit 3 fault status 3 register | 32-bit bitfield | 129 |  | IREG_15430 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0129_Inv_[n]_unit_3_fault_status_3_register
793 |  | Counter | Inv [n] unit 3 node status register | 32-bit bitfield | 130 |  | IREG_15434 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0130_Inv_[n]_unit_3_node_status_register
794 |  | Counter | Inv [n] unit 3 working status register | 32-bit bitfield | 131 |  | IREG_15448 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0131_Inv_[n]_unit_3_working_status_register
795 |  | Counter | Inv [n] unit 3 alarm status register | 32-bit bitfield | 132 |  | IREG_15450 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0132_Inv_[n]_unit_3_alarm_status_register
796 |  | Counter | Inv [n] unit 3 running status register | 32-bit bitfield | 133 |  | IREG_15502 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0133_Inv_[n]_unit_3_running_status_register
797 |  | Counter | Inv [n] unit 4 fault status 1 register | 32-bit bitfield | 134 |  | IREG_15546 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0134_Inv_[n]_unit_4_fault_status_1_register
798 |  | Counter | Inv [n] unit 4 fault status 2 register | 32-bit bitfield | 135 |  | IREG_15548 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0135_Inv_[n]_unit_4_fault_status_2_register
799 |  | Counter | Inv [n] unit 4 fault status 3 register | 32-bit bitfield | 136 |  | IREG_15550 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0136_Inv_[n]_unit_4_fault_status_3_register
800 |  | Counter | Inv [n] unit 4 node status register | 32-bit bitfield | 137 |  | IREG_15554 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0137_Inv_[n]_unit_4_node_status_register
801 |  | Counter | Inv [n] unit 4 working status register | 32-bit bitfield | 138 |  | IREG_15568 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0138_Inv_[n]_unit_4_working_status_register
802 |  | Counter | Inv [n] unit 4 alarm status register | 32-bit bitfield | 139 |  | IREG_15570 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0139_Inv_[n]_unit_4_alarm_status_register
803 |  | Counter | Inv [n] unit 4 running status register | 32-bit bitfield | 140 |  | IREG_15622 |  |  |  | unitless | 1 | [6 empty] | Change events | Not Shown | CNT_0140_Inv_[n]_unit_4_running_status_register
804 | Available | Binary input | Inv [n] any alarm | Boolean | 0 |  | PPC Logic | None | Alarm | Normal | [8 empty] | Change events | KPI | BI_0000_Inv_[n]_any_alarm |  |  | Alarms/AnyAlarm
805 | Available | Binary input | Inv [n] any fault | Boolean | 1 |  | PPC Logic | None | Alarm | Normal | [8 empty] | Change events | KPI | BI_0001_Inv_[n]_any_fault |  |  | Alarms/AnyFault
806 | Available | Binary input | Inv [n] communication failure alarm | Boolean | 2 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | Change events | KPI | BI_0002_Inv_[n]_communication_failure_alarm |  |  | Alarms/CommunicationFailureAlarm
807 | Available | Binary input | Inv [n] manual control status | Boolean | 3 |  | PPC Logic | On (1) | Manual | Auto | [8 empty] | Change events | KPI | BI_0003_Inv_[n]_manual_control_status |  |  | Status/InManualControl
808 | Available | Analog output | Inv [n] manual active power setpoint | 32-bit float | 0 |  | PPC Logic |  |  |  | kW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AO_0000_Inv_[n]_manual_active_power_setpoint_kW
809 | Available | Analog output | Inv [n] manual reactive power setpoint | 32-bit float | 1 |  | PPC Logic |  |  |  | kvar or PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | Primary Detail | AO_0001_Inv_[n]_manual_reactive_power_setpoint_kvar or PU
810 | Available | Analog output | Inv [n] manual reactive power mode | 32-bit signed integer | 2 |  | PPC Logic |  |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Primary Detail | AO_0002_Inv_[n]_manual_reactive_power_mode_enumeration | 0 to 2 | Voltage, Q(U) and Q(P) modes are not selectable through the HMI
811 | Available | Binary output | Inv [n] manual control | Boolean | 0 |  | PPC Logic | None | Manual | Auto | [8 empty] | Change events | Primary Detail | BO_0000_Inv_[n]_manual_control
812 | Available | Binary output | Inv [n] manual start stop | Boolean | 1 |  | PPC Logic | None | Start | Stop | [8 empty] | Change events | Primary Detail | BO_0001_Inv_[n]_manual_start_stop
813 | Available | Binary output | Inv [n] remote emergency stop | Boolean | 2 |  | HREG_15006 | None | E-stop | Normal | [8 empty] | Change events | Primary Detail | BO_0002_Inv_[n]_remote_emergency_stop
814 | Available | Binary output | Inv [n] manual DC switch open close | Boolean | 3 |  | HREG_15059 | None | Close | Open | [8 empty] | Change events | Primary Detail | BO_0003_Inv_[n]_manual_DC_switch_open_close

## PPC to Ignition - Environmental
Site Name | [5 empty] | DNP3.0 |  |  | PPC to Ignition - Environmental
Last updated |  | 2025-03-25 | Device Type | PPC |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire. | [9 empty] | Env Locations
Index digits in name |  | 4 | Subsystem / Zone | Environmental
|  |  | Number of multi-instrument towers | 10 |  |  |  |  | Replace [n] with environmental instrument station number written as 2 digits | [9 empty] | ENV-01 | ENV-02 | ENV-03 | ENV-04 | ENV-05 | ENV-06 | ENV-07 | ENV-08 | ENV-09 | ENV-10
|  |  | Number of standalone POA pyranometers | 0 |  |  |  |  | Replace [p] with standalone pyranometer instrument number written as 2 digits | [9 empty] | Block 4 | Block 12 | Block 24 | Block 30 | Block 41 | Block 55 | Block 63 | Block 73 | Block 84 | Block 93
|  |  | Number of soiling stations | 6 |  |  |  |  | Replace [s] with soiling station instrument number written as 2 digits | [9 empty] | ENV-11 | ENV-12 | ENV-13 | ENV-14 | ENV-15 | ENV-16
|  |  | Number of albedometers | 0 |  |  |  |  | Replace [a] with albedometer instrument number written as 2 digits | [9 empty] | Block 4 | Block 24 | Block 30 | Block 63 | Block 73 | Block 84
List Index | Availability | Object | Point Description | Data Type | DNP index | Bit | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | ENV-01: Historian Profile; ENV-02: HMI Category; ENV-03: RTAC Point Name; ENV-04: Enumeration Table; ENV-05: Comments
1 | Available | Analog input | Env [n] solar zenith angle | 32-bit float | 0 |  | HREG_0016 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0000_Env_[n]_solar_zenith_angle_degrees
2 | Available | Analog input | Env [n] solar elevation angle | 32-bit float | 1 |  | HREG_0018 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0001_Env_[n]_solar_elevation_angle_degrees
3 | Available | Analog input | Env [n] solar azimuth angle | 32-bit float | 2 |  | HREG_0020 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0002_Env_[n]_solar_azimuth_angle_degrees
4 | Available | Analog input | Env [n] POA irradiance raw | 32-bit float | 3 |  | HREG_0046 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0003_Env_[n]_POA_irradiance_raw_W_per_m2
5 | Available | Analog input | Env [n] POA irradiance temperature compensated | 32-bit float | 4 |  | HREG_0048 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0004_Env_[n]_POA_irradiance_temperature_compensated_W_per_m2
6 | Available | Analog input | Env [n] POA temperature | 32-bit float | 5 |  | HREG_0050 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0005_Env_[n]_POA_temperature_degC
7 | Available | Analog input | Env [n] POA tilt angle | 32-bit float | 6 |  | HREG_0354 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0006_Env_[n]_POA_tilt_angle_degrees
8 | Available | Analog input | Env [n] GHI irradiance raw | 32-bit float | 7 |  | HREG_0052 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0007_Env_[n]_GHI_irradiance_raw_W_per_m2
9 | Available | Analog input | Env [n] GHI irradiance temperature compensated | 32-bit float | 8 |  | HREG_0054 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0008_Env_[n]_GHI_irradiance_temperature_compensated_W_per_m2
10 | Available | Analog input | Env [n] GHI temperature | 32-bit float | 9 |  | HREG_0056 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0009_Env_[n]_GHI_temperature_degC
11 | Available | Analog input | Env [n] ambient temp | 32-bit float | 10 |  | HREG_0074 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0010_Env_[n]_ambient_temp_degC
12 | Available | Analog input | Env [n] dew point | 32-bit float | 11 |  | HREG_0076 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0011_Env_[n]_dew_point_degC
13 | Available | Analog input | Env [n] relative humidity | 32-bit float | 12 |  | HREG_0078 |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0012_Env_[n]_relative_humidity_pct
14 | Available | Analog input | Env [n] wind speed | 32-bit float | 13 |  | HREG_0080 |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0013_Env_[n]_wind_speed_m_per_s
15 | Available | Analog input | Env [n] wind speed max | 32-bit float | 14 |  | HREG_0082 |  |  |  | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0014_Env_[n]_wind_speed_max_m_per_s
16 | Available | Analog input | Env [n] wind direction | 32-bit float | 15 |  | HREG_0084 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0015_Env_[n]_wind_direction_degrees
17 | Available | Analog input | Env [n] wind quality | 32-bit float | 16 |  | HREG_0086 |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0016_Env_[n]_wind_quality_pct
18 | Available | Analog input | Env [n] barometric pressure local | 32-bit float | 17 |  | HREG_0088 |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0017_Env_[n]_barometric_pressure_local_mbar
19 | Available | Analog input | Env [n] barometric pressure sea level | 32-bit float | 18 |  | HREG_0090 |  |  |  | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0018_Env_[n]_barometric_pressure_sea_level_mbar
20 | Available | Analog input | Env [n] wind sensor compass | 32-bit float | 19 |  | HREG_0092 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0019_Env_[n]_wind_sensor_compass_degrees
21 | Available | Analog input | Env [n] wind chill | 32-bit float | 20 |  | HREG_0094 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0020_Env_[n]_wind_chill_degC
22 | Available | Analog input | Env [n] heat index | 32-bit float | 21 |  | HREG_0096 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0021_Env_[n]_heat_index_degC
23 | Available | Analog input | Env [n] rainfall total monthly | 32-bit float | 22 |  | PPC Logic |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0022_Env_[n]_rainfall_total_monthly_mm
24 | Available | Analog input | Env [n] rainfall instantaneous | 32-bit float | 23 |  | PPC Logic |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0023_Env_[n]_rainfall_instantaneous_mm
25 | Available | Analog input | Env [n] rainfall intensity instantaneous | 32-bit float | 24 |  | PPC Logic |  |  |  | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0024_Env_[n]_rainfall_intensity_instantaneous_mm_per_hr
26 | Available | Analog input | Env [n] rainfall total today | 32-bit float | 25 |  | HREG_0108 |  |  |  | mm | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0025_Env_[n]_rainfall_total_today_mm
27 | Available | Analog input | Env [n] BOM temperature 1 | 32-bit float | 26 |  | HREG_0124 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0026_Env_[n]_BOM_temperature_1_degC
28 | Available | Analog input | Env [n] BOM temperature 2 | 32-bit float | 27 |  | HREG_0126 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0027_Env_[n]_BOM_temperature_2_degC
29 | Not Available | Analog input | Env [n] BOM temperature 3 | 32-bit float | 28 |  | HREG_0128 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0028_Env_[n]_BOM_temperature_3_degC
30 | Available | Analog input | Env [n] data logger scan count | 32-bit float | 29 |  | HREG_0000 |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0029_Env_[n]_data_logger_scan_count_count
31 | Available | Analog input | Env [n] data logger skipped scans | 32-bit float | 30 |  | HREG_0002 |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0030_Env_[n]_data_logger_skipped_scans_count
32 | Available | Analog input | Env [n] data logger power supply voltage | 32-bit float | 31 |  | HREG_0004 |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0031_Env_[n]_data_logger_power_supply_voltage_V
33 | Available | Analog input | Env [n] data logger cabinet temperature | 32-bit float | 32 |  | HREG_0006 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0032_Env_[n]_data_logger_cabinet_temperature_degC
34 | Available | Analog input | Env [n] data logger battery backup voltage | 32-bit float | 33 |  | HREG_0010 |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0033_Env_[n]_data_logger_battery_backup_voltage_V
35 | Available | Analog input | Env [n] data logger battery backup charging source | 32-bit float | 34 |  | HREG_0040 |  |  |  | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0034_Env_[n]_data_logger_battery_backup_charging_source_enumeration; ENV-04: 0 thru 2; ENV-05: 0 = None, 1 = Solar, 2 = AC Power
36 | Available | Analog input | Env [n] reflected POA irradiance raw | 32-bit float | 35 |  | HREG_0746 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0035_Env_[n]_reflected_POA_irradiance_raw_W_per_m2
37 | Available | Analog input | Env [n] reflected POA irradiance temperature compensated | 32-bit float | 36 |  | HREG_0748 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0036_Env_[n]_reflected_POA_irradiance_temperature_compensated_W_per_m2
38 | Available | Analog input | Env [n] reflected POA temperature | 32-bit float | 37 |  | HREG_0750 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0037_Env_[n]_reflected_POA_temperature_degC
39 | Available | Analog input | Env [n] reflected insolation | 32-bit float | 38 |  | HREG_0753 |  |  |  | Wh/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0038_Env_[n]_reflected_insolation_Wh_per_m2
40 | Available | Analog input | Env [n] reflected POA tilt angle | 32-bit float | 39 |  | HREG_0774 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0039_Env_[n]_reflected_POA_tilt_angle_degrees
41 | Available | Analog input | Env [n] spare analog 01 | 32-bit float | 40 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0040_Env_[n]_spare_analog_01
42 | Available | Analog input | Env [n] spare analog 02 | 32-bit float | 41 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0041_Env_[n]_spare_analog_02
43 | Available | Analog input | Env [n] spare analog 03 | 32-bit float | 42 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0042_Env_[n]_spare_analog_03
44 | Available | Analog input | Env [n] spare analog 04 | 32-bit float | 43 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0043_Env_[n]_spare_analog_04
45 | Available | Analog input | Env [n] spare analog 05 | 32-bit float | 44 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0044_Env_[n]_spare_analog_05
46 | Available | Analog input | Env [p] POA irradiance raw | 32-bit float | 45 |  | HREG_0004 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0045_Env_[p]_POA_irradiance_raw_W_per_m2
47 | Available | Analog input | Env [p] POA irradiance temperature compensated | 32-bit float | 46 |  | HREG_0002 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0046_Env_[p]_POA_irradiance_temperature_compensated_W_per_m2
48 | Available | Analog input | Env [p] POA temperature | 32-bit float | 47 |  | HREG_0006 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0047_Env_[p]_POA_temperature_degC
49 | Available | Analog input | Env [p] POA tilt angle | 32-bit float | 48 |  | HREG_0194 |  |  |  | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0048_Env_[p]_POA_tilt_angle_degrees
50 | Available | Analog input | Env [p] spare analog 01 | 32-bit float | 49 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0049_Env_[p]_spare_analog_01
51 | Available | Analog input | Env [p] spare analog 02 | 32-bit float | 50 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0050_Env_[p]_spare_analog_02
52 | Available | Analog input | Env [s] soiling ratio raw | 32-bit float | 51 |  | HREG_0152 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0051_Env_[s]_soiling_ratio_raw
53 | Available | Analog input | Env [s] soiling ratio irradiance weighted | 32-bit float | 52 |  | HREG_0144 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0052_Env_[s]_soiling_ratio_irradiance_weighted
54 | Available | Analog input | Env [s] soiling loss factor raw | 32-bit float | 53 |  | HREG_0150 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0053_Env_[s]_soiling_loss_factor_raw
55 | Available | Analog input | Env [s] soiling loss factor irradiance weighted | 32-bit float | 54 |  | HREG_0142 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0054_Env_[s]_soiling_loss_factor_irradiance_weighted
56 | Available | Analog input | Env [s] clean panel short circuit current | 32-bit float | 55 |  | HREG_0138 |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0055_Env_[s]_clean_panel_short_circuit_current_A
57 | Available | Analog input | Env [s] soiled panel short circuit current | 32-bit float | 56 |  | HREG_0140 |  |  |  | A | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0056_Env_[s]_soiled_panel_short_circuit_current_A
58 | Available | Analog input | Env [s] short circuit current normalization ratio | 32-bit float | 57 |  | HREG_0154 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0057_Env_[s]_short_circuit_current_normalization_ratio; ENV-05: ISC clean / ISC soiled at time of normalization
59 | Available | Analog input | Env [s] clean panel effective irradiance | 32-bit float | 58 |  | HREG_0156 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0058_Env_[s]_clean_panel_effective_irradiance_W_per_m2
60 | Available | Analog input | Env [s] soiled panel effective irradiance | 32-bit float | 59 |  | HREG_0158 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0059_Env_[s]_soiled_panel_effective_irradiance_W_per_m2
61 | Available | Analog input | Env [s] clean panel BOM temperature | 32-bit float | 60 |  | HREG_0146 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0060_Env_[s]_clean_panel_BOM_temperature_degC
62 | Available | Analog input | Env [s] soiled panel BOM temperature | 32-bit float | 61 |  | HREG_0148 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0061_Env_[s]_soiled_panel_BOM_temperature_degC
63 | Available | Analog input | Env [s] soiling quality | 32-bit float | 62 |  | HREG_0616 |  |  |  | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0062_Env_[s]_soiling_quality_pct; ENV-05: Percent of possible samples that were actually sampled
64 | Available | Analog input | Env [s] number of days since last clear sky | 32-bit float | 63 |  | HREG_0618 |  |  |  | days | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0063_Env_[s]_number_of_days_since_last_clear_sky_days
65 | Available | Analog input | Env [s] data logger scan count | 32-bit float | 64 |  | HREG_0000 |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0064_Env_[s]_data_logger_scan_count_count
66 | Available | Analog input | Env [s] data logger skipped scans | 32-bit float | 65 |  | HREG_0002 |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0065_Env_[s]_data_logger_skipped_scans_count
67 | Available | Analog input | Env [s] data logger power supply voltage | 32-bit float | 66 |  | HREG_0004 |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0066_Env_[s]_data_logger_power_supply_voltage_V
68 | Available | Analog input | Env [s] data logger cabinet temperature | 32-bit float | 67 |  | HREG_0006 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0067_Env_[s]_data_logger_cabinet_temperature_degC
69 | Available | Analog input | Env [s] data logger battery backup voltage | 32-bit float | 68 |  | HREG_0010 |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0068_Env_[s]_data_logger_battery_backup_voltage_V
70 | Available | Analog input | Env [s] spare analog 01 | 32-bit float | 69 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0069_Env_[s]_spare_analog_01
71 | Available | Analog input | Env [s] spare analog 02 | 32-bit float | 70 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0070_Env_[s]_spare_analog_02
72 | Available | Analog input | Env [s] spare analog 03 | 32-bit float | 71 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0071_Env_[s]_spare_analog_03
73 | Available | Analog input | Env [s] spare analog 04 | 32-bit float | 72 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0072_Env_[s]_spare_analog_04
74 | Available | Analog input | Env [s] spare analog 05 | 32-bit float | 73 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0073_Env_[s]_spare_analog_05
75 | Available | Analog input | Env [s] spare analog 06 | 32-bit float | 74 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0074_Env_[s]_spare_analog_06
76 | Available | Analog input | Env [a] instantaneous albedo raw | 32-bit float | 75 |  | HREG_0608 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0075_Env_[a]_instantaneous_albedo_raw
77 | Available | Analog input | Env [a] instantaneous albedo temperature compensated | 32-bit float | 76 |  | HREG_0610 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: KPI; ENV-03: AI_0076_Env_[a]_instantaneous_albedo_temperature_compensated
78 | Available | Analog input | Env [a] daily average albedo raw | 32-bit float | 77 |  | HREG_0612 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0077_Env_[a]_daily_average_albedo_raw
79 | Available | Analog input | Env [a] daily average albedo temperature compensated | 32-bit float | 78 |  | HREG_0614 |  |  |  | unitless | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0078_Env_[a]_daily_average_albedo_temperature_compensated
80 | Available | Analog input | Env [a] GHI irradiance raw | 32-bit float | 79 |  | HREG_0596 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0079_Env_[a]_GHI_irradiance_raw_W_per_m2
81 | Available | Analog input | Env [a] GHI irradiance temperature compensated | 32-bit float | 80 |  | HREG_0598 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0080_Env_[a]_GHI_irradiance_temperature_compensated_W_per_m2
82 | Available | Analog input | Env [a] GHI temperature | 32-bit float | 81 |  | HREG_0600 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0081_Env_[a]_GHI_temperature_degC
83 | Available | Analog input | Env [a] RHI irradiance raw | 32-bit float | 82 |  | HREG_0602 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0082_Env_[a]_RHI_irradiance_raw_W_per_m2
84 | Available | Analog input | Env [a] RHI irradiance temperature compensated | 32-bit float | 83 |  | HREG_0604 |  |  |  | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0083_Env_[a]_RHI_irradiance_temperature_compensated_W_per_m2
85 | Available | Analog input | Env [a] RHI temperature | 32-bit float | 84 |  | HREG_0606 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: High resolution; ENV-02: Primary Detail; ENV-03: AI_0084_Env_[a]_RHI_temperature_degC
86 | Available | Analog input | Env [a] data logger scan count | 32-bit float | 85 |  | HREG_0000 |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0085_Env_[a]_data_logger_scan_count_count
87 | Available | Analog input | Env [a] data logger skipped scans | 32-bit float | 86 |  | HREG_0002 |  |  |  | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0086_Env_[a]_data_logger_skipped_scans_count
88 | Available | Analog input | Env [a] data logger power supply voltage | 32-bit float | 87 |  | HREG_0004 |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0087_Env_[a]_data_logger_power_supply_voltage_V
89 | Available | Analog input | Env [a] data logger cabinet temperature | 32-bit float | 88 |  | HREG_0006 |  |  |  | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0088_Env_[a]_data_logger_cabinet_temperature_degC
90 | Available | Analog input | Env [a] data logger battery backup voltage | 32-bit float | 89 |  | HREG_0010 |  |  |  | V | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | ENV-01: Low resolution; ENV-02: Diagnostic; ENV-03: AI_0089_Env_[a]_data_logger_battery_backup_voltage_V
91 | Available | Analog input | Env [a] spare analog 01 | 32-bit float | 90 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0090_Env_[a]_spare_analog_01
92 | Available | Analog input | Env [a] spare analog 02 | 32-bit float | 91 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0091_Env_[a]_spare_analog_02
93 | Available | Analog input | Env [a] spare analog 03 | 32-bit float | 92 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0092_Env_[a]_spare_analog_03
94 | Available | Analog input | Env [a] spare analog 04 | 32-bit float | 93 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0093_Env_[a]_spare_analog_04
95 | Available | Analog input | Env [a] spare analog 05 | 32-bit float | 94 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0094_Env_[a]_spare_analog_05
96 | Available | Analog input | Env [a] spare analog 06 | 32-bit float | 95 | [7 empty] | -3.4028e+38 | 3.4028e+38 |  |  |  |  | ENV-03: AI_0095_Env_[a]_spare_analog_06
97 | Available | Counter | Env [n] data logger alarms register | 32-bit bitfield | 0 |  | HREG_2002 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0000_Env_[n]_data_logger_alarms_register
98 | Available | Counter | Env [n] data logger watchdog error | 32-bit bitfield | 0 | 0 | HREG_2002.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_watchdog_error
99 | Available | Counter | Env [n] data logger skipped main scan | 32-bit bitfield | 0 | 1 | HREG_2002.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_skipped_main_scan
100 | Available | Counter | Env [n] data logger skipped slow scan | 32-bit bitfield | 0 | 2 | HREG_2002.2 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_skipped_slow_scan
101 | Available | Counter | Env [n] data logger program variable out of bounds | 32-bit bitfield | 0 | 3 | HREG_2002.3 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_program_variable_out_of_bounds
102 | Available | Counter | Env [n] data logger low 12V | 32-bit bitfield | 0 | 4 | HREG_2002.4 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_low_12V
103 | Available | Counter | Env [n] data logger low 5V | 32-bit bitfield | 0 | 5 | HREG_2002.5 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_low_5V
104 | Available | Counter | Env [n] data logger lithium battery error | 32-bit bitfield | 0 | 8 | HREG_2002.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_lithium_battery_error
105 | Available | Counter | Env [n] data logger lithium battery low | 32-bit bitfield | 0 | 9 | HREG_2002.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_lithium_battery_low
106 | Available | Counter | Env [n] data logger lithium battery critical | 32-bit bitfield | 0 | 10 | HREG_2002.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_lithium_battery_critical
107 | Available | Counter | Env [n] data logger voltage error | 32-bit bitfield | 0 | 16 | HREG_2002.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_voltage_error
108 | Available | Counter | Env [n] data logger low voltage warning | 32-bit bitfield | 0 | 17 | HREG_2002.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_low_voltage_warning
109 | Available | Counter | Env [n] data logger low voltage | 32-bit bitfield | 0 | 18 | HREG_2002.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_low_voltage
110 | Available | Counter | Env [n] data logger over voltage | 32-bit bitfield | 0 | 19 | HREG_2002.19 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_over_voltage
111 | Available | Counter | Env [n] data logger temperature error | 32-bit bitfield | 0 | 24 | HREG_2002.24 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_temperature_error
112 | Available | Counter | Env [n] data logger temperature below operating range | 32-bit bitfield | 0 | 25 | HREG_2002.25 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_temperature_below_operating_range
113 | Available | Counter | Env [n] data logger temperature above operating range | 32-bit bitfield | 0 | 26 | HREG_2002.26 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0000_Env_[n]_data_logger_temperature_above_operating_range
114 | Available | Counter | Env [n] battery alarms register | 32-bit bitfield | 1 |  | HREG_2004 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0001_Env_[n]_battery_alarms_register
115 | Available | Counter | Env [n] check battery | 32-bit bitfield | 1 | 0 | HREG_2004.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_check_battery
116 | Available | Counter | Env [n] battery voltage error | 32-bit bitfield | 1 | 8 | HREG_2004.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_battery_voltage_error
117 | Available | Counter | Env [n] low battery voltage warning | 32-bit bitfield | 1 | 9 | HREG_2004.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_low_battery_voltage_warning
118 | Available | Counter | Env [n] low battery voltage critical | 32-bit bitfield | 1 | 10 | HREG_2004.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_low_battery_voltage_critical
119 | Available | Counter | Env [n] low battery voltage deep discharge | 32-bit bitfield | 1 | 11 | HREG_2004.11 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_low_battery_voltage_deep_discharge
120 | Available | Counter | Env [n] battery current error | 32-bit bitfield | 1 | 16 | HREG_2004.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_battery_current_error
121 | Available | Counter | Env [n] excessive battery current warning | 32-bit bitfield | 1 | 17 | HREG_2004.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_excessive_battery_current_warning
122 | Available | Counter | Env [n] excessive battery current critical | 32-bit bitfield | 1 | 18 | HREG_2004.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0001_Env_[n]_excessive_battery_current_critical
123 | Available | Counter | Env [n] charging alarms register | 32-bit bitfield | 2 |  | HREG_2006 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0002_Env_[n]_charging_alarms_register
124 | Available | Counter | Env [n] input voltage error | 32-bit bitfield | 2 | 0 | HREG_2006.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_input_voltage_error
125 | Available | Counter | Env [n] rpu enabled | 32-bit bitfield | 2 | 1 | HREG_2006.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_rpu_enabled
126 | Available | Counter | Env [n] input current error | 32-bit bitfield | 2 | 8 | HREG_2006.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_input_current_error
127 | Available | Counter | Env [n] excessive input current | 32-bit bitfield | 2 | 9 | HREG_2006.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_excessive_input_current
128 | Available | Counter | Env [n] load current error | 32-bit bitfield | 2 | 16 | HREG_2006.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_load_current_error
129 | Available | Counter | Env [n] excessive load current warning | 32-bit bitfield | 2 | 17 | HREG_2006.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_excessive_load_current_warning
130 | Available | Counter | Env [n] excessive load current | 32-bit bitfield | 2 | 18 | HREG_2006.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0002_Env_[n]_excessive_load_current
131 | Available | Counter | Env [n] GHI alarms register | 32-bit bitfield | 3 |  | HREG_2018 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0003_Env_[n]_GHI_alarms_register
132 | Available | Counter | Env [n] GHI irradiance error | 32-bit bitfield | 3 | 0 | HREG_2018.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_irradiance_error
133 | Available | Counter | Env [n] GHI irradiance negative | 32-bit bitfield | 3 | 1 | HREG_2018.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_irradiance_negative
134 | Available | Counter | Env [n] GHI irradiance above solar constant | 32-bit bitfield | 3 | 2 | HREG_2018.2 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_irradiance_above_solar_constant
135 | Available | Counter | Env [n] GHI temperature corrected irradiance error | 32-bit bitfield | 3 | 8 | HREG_2018.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_temperature_corrected_irradiance_error
136 | Available | Counter | Env [n] GHI temperature corrected irradiance negative | 32-bit bitfield | 3 | 9 | HREG_2018.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_temperature_corrected_irradiance_negative
137 | Available | Counter | Env [n] GHI temperature corrected irradiance above solar constant | 32-bit bitfield | 3 | 10 | HREG_2018.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_temperature_corrected_irradiance_above_solar_constant
138 | Available | Counter | Env [n] GHI case temperature error | 32-bit bitfield | 3 | 16 | HREG_2018.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_case_temperature_error
139 | Available | Counter | Env [n] GHI case temperature below operating range | 32-bit bitfield | 3 | 17 | HREG_2018.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_case_temperature_below_operating_range
140 | Available | Counter | Env [n] GHI case temperature above operating range | 32-bit bitfield | 3 | 18 | HREG_2018.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_case_temperature_above_operating_range
141 | Available | Counter | Env [n] GHI irradiance insufficient activity | 32-bit bitfield | 3 | 31 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_GHI_irradiance_insufficient_activity
142 | Available | Counter | Env [n] POA alarms register | 32-bit bitfield | 4 |  | HREG_2020 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0004_Env_[n]_POA_alarms_register
143 | Available | Counter | Env [n] POA irradiance error | 32-bit bitfield | 3 | 0 | HREG_2020.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_irradiance_error
144 | Available | Counter | Env [n] POA irradiance negative | 32-bit bitfield | 3 | 1 | HREG_2020.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_irradiance_negative
145 | Available | Counter | Env [n] POA irradiance above solar constant | 32-bit bitfield | 3 | 2 | HREG_2020.2 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_irradiance_above_solar_constant
146 | Available | Counter | Env [n] POA temperature corrected irradiance error | 32-bit bitfield | 3 | 8 | HREG_2020.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_temperature_corrected_irradiance_error
147 | Available | Counter | Env [n] POA temperature corrected irradiance negative | 32-bit bitfield | 3 | 9 | HREG_2020.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_temperature_corrected_irradiance_negative
148 | Available | Counter | Env [n] POA temperature corrected irradiance above solar constant | 32-bit bitfield | 3 | 10 | HREG_2020.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_temperature_corrected_irradiance_above_solar_constant
149 | Available | Counter | Env [n] POA case temperature error | 32-bit bitfield | 3 | 16 | HREG_2020.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_case_temperature_error
150 | Available | Counter | Env [n] POA case temperature below operating range | 32-bit bitfield | 3 | 17 | HREG_2020.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_case_temperature_below_operating_range
151 | Available | Counter | Env [n] POA case temperature above operating range | 32-bit bitfield | 3 | 18 | HREG_2020.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_case_temperature_above_operating_range
152 | Available | Counter | Env [n] POA irradiance insufficient activity | 32-bit bitfield | 3 | 31 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0003_Env_[n]_POA_irradiance_insufficient_activity
153 | Available | Counter | Env [n] multifunction alarms register | 32-bit bitfield | 5 |  | HREG_2038 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0005_Env_[n]_multifunction_alarms_register
154 | Available | Counter | Env [n] ambient temperature error | 32-bit bitfield | 4 | 0 | HREG_2038.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_ambient_temperature_error
155 | Available | Counter | Env [n] ambient temperature below operating range | 32-bit bitfield | 4 | 1 | HREG_2038.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_ambient_temperature_below_operating_range
156 | Available | Counter | Env [n] ambient temperature above operating range | 32-bit bitfield | 4 | 2 | HREG_2038.2 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_ambient_temperature_above_operating_range
157 | Available | Counter | Env [n] dew point error | 32-bit bitfield | 4 | 3 | HREG_2038.3 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_dew_point_error
158 | Available | Counter | Env [n] dew point above ambient temperature | 32-bit bitfield | 4 | 4 | HREG_2038.4 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_dew_point_above_ambient_temperature
159 | Available | Counter | Env [n] condensation warning | 32-bit bitfield | 4 | 5 | HREG_2038.5 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_condensation_warning
160 | Available | Counter | Env [n] relative humidity error | 32-bit bitfield | 4 | 8 | HREG_2038.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_relative_humidity_error
161 | Available | Counter | Env [n] relative humidity below operating range | 32-bit bitfield | 4 | 9 | HREG_2038.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_relative_humidity_below_operating_range
162 | Available | Counter | Env [n] relative humidity above operating range | 32-bit bitfield | 4 | 10 | HREG_2038.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_relative_humidity_above_operating_range
163 | Available | Counter | Env [n] absolute barometric pressure error | 32-bit bitfield | 4 | 16 | HREG_2038.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_absolute_barometric_pressure_error
164 | Available | Counter | Env [n] absolute barometric pressure below operating range | 32-bit bitfield | 4 | 17 | HREG_2038.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_absolute_barometric_pressure_below_operating_range
165 | Available | Counter | Env [n] absolute barometric pressure above operating range | 32-bit bitfield | 4 | 18 | HREG_2038.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_absolute_barometric_pressure_above_operating_range
166 | Available | Counter | Env [n] sea level barometric pressure error | 32-bit bitfield | 4 | 24 | HREG_2038.24 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_sea_level_barometric_pressure_error
167 | Available | Counter | Env [n] sea level barometric pressure below operating range | 32-bit bitfield | 4 | 25 | HREG_2038.25 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_sea_level_barometric_pressure_below_operating_range
168 | Available | Counter | Env [n] sea level barometric pressure above operating range | 32-bit bitfield | 4 | 26 | HREG_2038.26 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0004_Env_[n]_sea_level_barometric_pressure_above_operating_range
169 | Available | Counter | Env [n] wind alarms register | 32-bit bitfield | 6 |  | HREG_2040 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0006_Env_[n]_wind_alarms_register
170 | Available | Counter | Env [n] wind speed error | 32-bit bitfield | 5 | 0 | HREG_2040.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_error
171 | Available | Counter | Env [n] wind speed below operating range | 32-bit bitfield | 5 | 1 | HREG_2040.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_below_operating_range
172 | Available | Counter | Env [n] wind speed above operating range | 32-bit bitfield | 5 | 2 | HREG_2040.2 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_above_operating_range
173 | Available | Counter | Env [n] wind speed unable to execute measurement due to ambient conditions | 32-bit bitfield | 5 | 3 | HREG_2040.3 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_unable_to_execute_measurement_due_to_ambient_conditions
174 | Available | Counter | Env [n] wind speed quality warning | 32-bit bitfield | 5 | 4 | HREG_2040.4 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_quality_warning
175 | Available | Counter | Env [n] wind speed quality error | 32-bit bitfield | 5 | 5 | HREG_2040.5 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_quality_error
176 | Available | Counter | Env [n] wind speed max error | 32-bit bitfield | 5 | 8 | HREG_2040.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_max_error
177 | Available | Counter | Env [n] wind speed max below operating range | 32-bit bitfield | 5 | 9 | HREG_2040.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_max_below_operating_range
178 | Available | Counter | Env [n] wind speed max above operating range | 32-bit bitfield | 5 | 10 | HREG_2040.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_max_above_operating_range
179 | Available | Counter | Env [n] wind direction error | 32-bit bitfield | 5 | 16 | HREG_2040.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_direction_error
180 | Available | Counter | Env [n] wind direction below operating range | 32-bit bitfield | 5 | 17 | HREG_2040.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_direction_below_operating_range
181 | Available | Counter | Env [n] wind direction above operating range | 32-bit bitfield | 5 | 18 | HREG_2040.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_direction_above_operating_range
182 | Available | Counter | Env [n] compass error | 32-bit bitfield | 5 | 24 | HREG_2040.24 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_compass_error
183 | Available | Counter | Env [n] compass below operating range | 32-bit bitfield | 5 | 25 | HREG_2040.25 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_compass_below_operating_range
184 | Available | Counter | Env [n] compass above operating range | 32-bit bitfield | 5 | 26 | HREG_2040.26 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_compass_above_operating_range
185 | Available | Counter | Env [n] wind speed insufficient activity | 32-bit bitfield | 5 | 31 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0005_Env_[n]_wind_speed_insufficient_activity
186 | Available | Counter | Env [n] rain alarms regsiter | 32-bit bitfield | 7 |  | HREG_2042 |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0007_Env_[n]_rain_alarms_regsiter
187 | Available | Counter | Env [n] rain total error | 32-bit bitfield | 6 | 0 | HREG_2042.0 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_total_error
188 | Available | Counter | Env [n] rain total negative | 32-bit bitfield | 6 | 1 | HREG_2042.1 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_total_negative
189 | Available | Counter | Env [n] rain total above operating range | 32-bit bitfield | 6 | 2 | HREG_2042.2 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_total_above_operating_range
190 | Available | Counter | Env [n] rain intensity error | 32-bit bitfield | 6 | 8 | HREG_2042.8 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_intensity_error
191 | Available | Counter | Env [n] rain intensity negative | 32-bit bitfield | 6 | 9 | HREG_2042.9 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_intensity_negative
192 | Available | Counter | Env [n] rain intensity above operating range | 32-bit bitfield | 6 | 10 | HREG_2042.10 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_intensity_above_operating_range
193 | Available | Counter | Env [n] rain today error | 32-bit bitfield | 6 | 16 | HREG_2042.16 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_today_error
194 | Available | Counter | Env [n] rain today is negative | 32-bit bitfield | 6 | 17 | HREG_2042.17 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_today_is_negative
195 | Available | Counter | Env [n] rain today above operating range | 32-bit bitfield | 6 | 18 | HREG_2042.18 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0006_Env_[n]_rain_today_above_operating_range
196 | Available | Counter | Env [n] BOM alarm register | 32-bit bitfield | 8 |  | PPC Logic |  |  |  | unitless | 1 | [6 empty] | ENV-01: Change Events; ENV-02: Not Shown; ENV-03: CNT_0008_Env_[n]_BOM_alarm_register
197 | Available | Counter | Env [n] BOM 1 temperature error | 32-bit bitfield | 7 | 0 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_1_temperature_error
198 | Available | Counter | Env [n] BOM 1 temperature below operating range | 32-bit bitfield | 7 | 1 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_1_temperature_below_operating_range
199 | Available | Counter | Env [n] BOM 1 temperature above operating range | 32-bit bitfield | 7 | 2 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_1_temperature_above_operating_range
200 | Available | Counter | Env [n] BOM 2 temperature error | 32-bit bitfield | 7 | 3 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_2_temperature_error
201 | Available | Counter | Env [n] BOM 2 temperature below operating range | 32-bit bitfield | 7 | 4 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_2_temperature_below_operating_range
202 | Available | Counter | Env [n] BOM 2 temperature above operating range | 32-bit bitfield | 7 | 5 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_2_temperature_above_operating_range
203 | Available | Counter | Env [n] BOM 3 temperature error | 32-bit bitfield | 7 | 6 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_3_temperature_error
204 | Available | Counter | Env [n] BOM 3 temperature below operating range | 32-bit bitfield | 7 | 7 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_3_temperature_below_operating_range
205 | Available | Counter | Env [n] BOM 3 temperature above operating range | 32-bit bitfield | 7 | 8 | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: CNT_0007_Env_[n]_BOM_3_temperature_above_operating_range
206 | Available | Binary input | Env [n] summary alarm | Boolean | 0 |  | HREG_2000 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0000_Env_[n]_summary_alarm
207 | Available | Binary input | Env [n] maintenance button pressed | Boolean | 1 |  | HREG_0026 | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0001_Env_[n]_maintenance_button_pressed
208 | Available | Binary input | Env [n] pyranometer heat status | Boolean | 2 |  | HREG_0022 | None | On | Off | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0002_Env_[n]_pyranometer_heat_status
209 | Available | Binary input | Env [n] communication failure alarm | Boolean | 3 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0003_Env_[n]_communication_failure_alarm
210 | Available | Binary input | Env [p] POA irradiance error | Boolean | 4 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0004_Env_[p]_POA_irradiance_error
211 | Available | Binary input | Env [p] POA irradiance negative | Boolean | 5 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0005_Env_[p]_POA_irradiance_negative
212 | Available | Binary input | Env [p] POA irradiance above solar constant | Boolean | 6 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0006_Env_[p]_POA_irradiance_above_solar_constant
213 | Available | Binary input | Env [p] POA temperature corrected irradiance error | Boolean | 7 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0007_Env_[p]_POA_temperature_corrected_irradiance_error
214 | Available | Binary input | Env [p] POA temperature corrected irradiance negative | Boolean | 8 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0008_Env_[p]_POA_temperature_corrected_irradiance_negative
215 | Available | Binary input | Env [p] POA temperature corrected irradiance above solar constant | Boolean | 9 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0009_Env_[p]_POA_temperature_corrected_irradiance_above_solar_constant
216 | Available | Binary input | Env [p] POA case temperature error | Boolean | 10 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0010_Env_[p]_POA_case_temperature_error
217 | Available | Binary input | Env [p] POA case temperature below operating range | Boolean | 11 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0011_Env_[p]_POA_case_temperature_below_operating_range
218 | Available | Binary input | Env [p] POA case temperature above operating range | Boolean | 12 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0012_Env_[p]_POA_case_temperature_above_operating_range
219 | Available | Binary input | Env [p] POA irradiance insufficient activity | Boolean | 13 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0013_Env_[p]_POA_irradiance_insufficient_activity
220 | Available | Binary input | Env [p] communication failure alarm | Boolean | 14 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0014_Env_[p]_communication_failure_alarm
221 | Available | Binary input | Env [s] soiling ratio out of range | Boolean | 15 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0015_Env_[s]_soiling_ratio_out_of_range
222 | Available | Binary input | Env [s] heavy soiling alarm | Boolean | 16 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0016_Env_[s]_heavy_soiling_alarm; ENV-05: Soiling ratio below 0.93
223 | Available | Binary input | Env [s] extremely heavy soiling alarm | Boolean | 17 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0017_Env_[s]_extremely_heavy_soiling_alarm; ENV-05: Soiling ratio below 0.87
224 | Available | Binary input | Env [s] soiling ratio insufficient activity | Boolean | 18 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0018_Env_[s]_soiling_ratio_insufficient_activity
225 | Available | Binary input | Env [s] clean panel BOM temperature error | Boolean | 19 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0019_Env_[s]_clean_panel_BOM_temperature_error
226 | Available | Binary input | Env [s] clean panel BOM temperature below operating range | Boolean | 20 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0020_Env_[s]_clean_panel_BOM_temperature_below_operating_range
227 | Available | Binary input | Env [s] clean panel BOM temperature above operating range | Boolean | 21 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0021_Env_[s]_clean_panel_BOM_temperature_above_operating_range
228 | Available | Binary input | Env [s] soiled panel BOM temperature error | Boolean | 22 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0022_Env_[s]_soiled_panel_BOM_temperature_error
229 | Available | Binary input | Env [s] soiled panel BOM temperature below operating range | Boolean | 23 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0023_Env_[s]_soiled_panel_BOM_temperature_below_operating_range
230 | Available | Binary input | Env [s] soiled panel BOM temperature above operating range | Boolean | 24 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0024_Env_[s]_soiled_panel_BOM_temperature_above_operating_range
231 | Available | Binary input | Env [s] BOM temperature difference too great | Boolean | 25 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0025_Env_[s]_BOM_temperature_difference_too_great
232 | Available | Binary input | Env [s] clean panel ISC out of range | Boolean | 26 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0026_Env_[s]_clean_panel_ISC_out_of_range
233 | Available | Binary input | Env [s] soiled panel ISC out of range | Boolean | 27 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0027_Env_[s]_soiled_panel_ISC_out_of_range
234 | Available | Binary input | Env [s] ISC difference too great | Boolean | 28 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0028_Env_[s]_ISC_difference_too_great
235 | Available | Binary input | Env [s] data logger watchdog error | Boolean | 29 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0029_Env_[s]_data_logger_watchdog_error
236 | Available | Binary input | Env [s] data logger skipped main scan | Boolean | 30 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0030_Env_[s]_data_logger_skipped_main_scan
237 | Available | Binary input | Env [s] data logger skipped slow scan | Boolean | 31 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0031_Env_[s]_data_logger_skipped_slow_scan
238 | Available | Binary input | Env [s] data logger program variable out of bounds | Boolean | 32 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0032_Env_[s]_data_logger_program_variable_out_of_bounds
239 | Available | Binary input | Env [s] data logger low 12V | Boolean | 33 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0033_Env_[s]_data_logger_low_12V
240 | Available | Binary input | Env [s] data logger low 5V | Boolean | 34 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0034_Env_[s]_data_logger_low_5V
241 | Available | Binary input | Env [s] data logger lithium battery error | Boolean | 35 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0035_Env_[s]_data_logger_lithium_battery_error
242 | Available | Binary input | Env [s] data logger lithium battery low | Boolean | 36 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0036_Env_[s]_data_logger_lithium_battery_low
243 | Available | Binary input | Env [s] data logger lithium battery critical | Boolean | 37 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0037_Env_[s]_data_logger_lithium_battery_critical
244 | Available | Binary input | Env [s] data logger voltage error | Boolean | 38 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0038_Env_[s]_data_logger_voltage_error
245 | Available | Binary input | Env [s] data logger low voltage warning | Boolean | 39 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0039_Env_[s]_data_logger_low_voltage_warning
246 | Available | Binary input | Env [s] data logger low voltage | Boolean | 40 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0040_Env_[s]_data_logger_low_voltage
247 | Available | Binary input | Env [s] data logger over voltage | Boolean | 41 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0041_Env_[s]_data_logger_over_voltage
248 | Available | Binary input | Env [s] data logger temperature error | Boolean | 42 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0042_Env_[s]_data_logger_temperature_error
249 | Available | Binary input | Env [s] data logger temperature below operating range | Boolean | 43 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0043_Env_[s]_data_logger_temperature_below_operating_range
250 | Available | Binary input | Env [s] data logger temperature above operating range | Boolean | 44 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0044_Env_[s]_data_logger_temperature_above_operating_range
251 | Available | Binary input | Env [s] communication failure alarm | Boolean | 45 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0045_Env_[s]_communication_failure_alarm
252 | Available | Binary input | Env [a] GHI irradiance error | Boolean | 46 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0046_Env_[a]_GHI_irradiance_error
253 | Available | Binary input | Env [a] GHI irradiance negative | Boolean | 47 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0047_Env_[a]_GHI_irradiance_negative
254 | Available | Binary input | Env [a] GHI irradiance above solar constant | Boolean | 48 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0048_Env_[a]_GHI_irradiance_above_solar_constant
255 | Available | Binary input | Env [a] GHI irradiance insufficient activity | Boolean | 49 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0049_Env_[a]_GHI_irradiance_insufficient_activity
256 | Available | Binary input | Env [a] RHI irradiance error | Boolean | 50 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0050_Env_[a]_RHI_irradiance_error
257 | Available | Binary input | Env [a] RHI irradiance negative | Boolean | 51 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0051_Env_[a]_RHI_irradiance_negative
258 | Available | Binary input | Env [a] RHI irradiance above solar constant | Boolean | 52 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0052_Env_[a]_RHI_irradiance_above_solar_constant
259 | Available | Binary input | Env [a] RHI irradiance insufficient activity | Boolean | 53 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0053_Env_[a]_RHI_irradiance_insufficient_activity
260 | Available | Binary input | Env [a] GHI case temperature error | Boolean | 54 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0054_Env_[a]_GHI_case_temperature_error
261 | Available | Binary input | Env [a] GHI case temperature below operating range | Boolean | 55 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0055_Env_[a]_GHI_case_temperature_below_operating_range
262 | Available | Binary input | Env [a] GHI case temperature above operating range | Boolean | 56 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0056_Env_[a]_GHI_case_temperature_above_operating_range
263 | Available | Binary input | Env [a] RHI case temperature error | Boolean | 57 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0057_Env_[a]_RHI_case_temperature_error
264 | Available | Binary input | Env [a] RHI case temperature below operating range | Boolean | 58 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0058_Env_[a]_RHI_case_temperature_below_operating_range
265 | Available | Binary input | Env [a] RHI case temperature above operating range | Boolean | 59 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0059_Env_[a]_RHI_case_temperature_above_operating_range
266 | Available | Binary input | Env [a] albedo out of range | Boolean | 60 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0060_Env_[a]_albedo_out_of_range
267 | Available | Binary input | Env [a] data logger watchdog error | Boolean | 61 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0061_Env_[a]_data_logger_watchdog_error
268 | Available | Binary input | Env [a] data logger skipped main scan | Boolean | 62 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0062_Env_[a]_data_logger_skipped_main_scan
269 | Available | Binary input | Env [a] data logger skipped slow scan | Boolean | 63 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0063_Env_[a]_data_logger_skipped_slow_scan
270 | Available | Binary input | Env [a] data logger program variable out of bounds | Boolean | 64 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0064_Env_[a]_data_logger_program_variable_out_of_bounds
271 | Available | Binary input | Env [a] data logger low 12V | Boolean | 65 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0065_Env_[a]_data_logger_low_12V
272 | Available | Binary input | Env [a] data logger low 5V | Boolean | 66 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0066_Env_[a]_data_logger_low_5V
273 | Available | Binary input | Env [a] data logger lithium battery error | Boolean | 67 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0067_Env_[a]_data_logger_lithium_battery_error
274 | Available | Binary input | Env [a] data logger lithium battery low | Boolean | 68 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0068_Env_[a]_data_logger_lithium_battery_low
275 | Available | Binary input | Env [a] data logger lithium battery critical | Boolean | 69 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0069_Env_[a]_data_logger_lithium_battery_critical
276 | Available | Binary input | Env [a] data logger voltage error | Boolean | 70 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0070_Env_[a]_data_logger_voltage_error
277 | Available | Binary input | Env [a] data logger low voltage warning | Boolean | 71 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0071_Env_[a]_data_logger_low_voltage_warning
278 | Available | Binary input | Env [a] data logger low voltage | Boolean | 72 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0072_Env_[a]_data_logger_low_voltage
279 | Available | Binary input | Env [a] data logger over voltage | Boolean | 73 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0073_Env_[a]_data_logger_over_voltage
280 | Available | Binary input | Env [a] data logger temperature error | Boolean | 74 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0074_Env_[a]_data_logger_temperature_error
281 | Available | Binary input | Env [a] data logger temperature below operating range | Boolean | 75 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0075_Env_[a]_data_logger_temperature_below_operating_range
282 | Available | Binary input | Env [a] data logger temperature above operating range | Boolean | 76 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0076_Env_[a]_data_logger_temperature_above_operating_range
283 | Available | Binary input | Env [a] communication failure alarm | Boolean | 77 |  | PPC Logic | On (1) | Alarm | Normal | [8 empty] | ENV-01: Change Events; ENV-02: Alarms; ENV-03: BI_0077_Env_[a]_communication_failure_alarm
Note on W5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Block 33 changed to Block 30 8/21/24
Note on Y5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Block 50 changed to Block 55 8/21/24
Note on V7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Block 33 changed to 30 8.21.24

## PPC to Ignition - PPC
Site Name | [5 empty] | DNP3.0 |  |  | PPC to Ignition - PPC
Last updated |  | 2023-06-05 | Device Type | PPC |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 4 | Subsystem / Zone | PPC
List Index | Availability | Object | Point Description | Data Type | DNP index | Bit | Device Point Name | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments | Ignt TagPath Prefix: [MidcontinentSolar]PPC/
1 | Available | Analog input | Plant status | 32-bit float | 0 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0000_Plant_status_enumeration | 0 thru 9 |  | Status/PlantStatusCode Status/PlantStatus_string
2 | Available | Analog input | Active power mode feedback | 32-bit float | 1 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0001_Active_power_mode_feedback_enumeration | 0 thru 2 |  | Control/ActivePower/ModeFeedbackCode Control/ActivePower/ModeFeedback_string
3 | Available | Analog input | Active power setpoint feedback | 32-bit float | 2 | [5 empty] | MW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0002_Active_power_setpoint_feedback_MW |  |  | Control/ActivePower/SetpointFeedback
4 | Available | Analog input | Reactive power mode feedback | 32-bit float | 3 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0003_Reactive_power_mode_feedback_enumeration | 0 thru 3 |  | Control/ReactivePower/ModeFeedbackCode Control/ReactivePower/ModeFeedback_string
5 | Available | Analog input | Voltage regulation setpoint feedback | 32-bit float | 4 | [5 empty] | kV | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0004_Voltage_regulation_setpoint_feedback_kV |  |  | Control/ReactivePower/VoltageRegulationSetpointFeedback
6 | Available | Analog input | Power factor regulation setpoint feedback | 32-bit float | 5 | [5 empty] | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0005_Power_factor_regulation_setpoint_feedback_PU |  |  | Control/ReactivePower/PFRegulationSetpointFeedback
7 | Available | Analog input | Var output regulation setpoint feedback | 32-bit float | 6 | [5 empty] | Mvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0006_Var_output_regulation_setpoint_feedback_Mvar |  |  | Control/ReactivePower/VarOutputRegulationSetpointFeedback
8 | Available | Analog input | Control command source feedback | 32-bit float | 7 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0007_Control_command_source_feedback_enumeration | 0 to 2 |  | Control/ControlCommandSourceFeedbackCode Control/ControlCommandSourceFeedback_string
9 | Available | Analog input | Setpoint source feedback | 32-bit float | 8 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0008_Setpoint_source_feedback_enumeration | 0 to 2 |  | Control/SetpointSourceFeedbackCode Control/SetpointSourceFeedback_string
10 | Available | Analog input | Generation output | 32-bit float | 9 | [5 empty] | MW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0009_Generation_output_MW |  |  | Metering/MWOut
11 | Available | Analog input | Reactive output | 32-bit float | 10 | [5 empty] | Mvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0010_Reactive_output_Mvar |  |  | Metering/MvarOut
12 | Available | Analog input | Median Line-Line Voltage | 32-bit float | 11 | [5 empty] | kV | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0011_System_voltage_kV |  | 3ph median ph-ph | Metering/kVAverage
13 | Available | Analog input | Power factor | 32-bit float | 12 | [5 empty] | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0012_Power_factor_PU |  |  | Metering/PF
14 | Available | Analog input | Frequency | 32-bit float | 13 | [5 empty] | Hz | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0013_Frequency_Hz |  |  | Metering/Hz
15 | Available | Analog input | Maximum available generation output | 32-bit float | 14 | [5 empty] | MW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0014_Maximum_available_generation_output_MW |  |  | Projections/MWOut_MaxAvailable
16 | Available | Analog input | Maximum available reactive source | 32-bit float | 15 | [5 empty] | Mvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0015_Maximum_available_reactive_source_Mvar |  |  | Projections/MvarSource_MaxAvailable
17 | Available | Analog input | Maximum available reactive sink | 32-bit float | 16 | [5 empty] | Mvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0016_Maximum_available_reactive_sink_Mvar |  |  | Projections/MvarSink_MaxAvailable
18 | Available | Analog input | Site average insolation | 32-bit float | 17 | [5 empty] | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0017_Site_average_insolation_W_per_m2 |  |  | Stats/SiteAvgInsolation
19 | Available | Analog input | Net energy generation today | 32-bit float | 18 | [5 empty] | MWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0018_Net_energy_generation_today_MWh |  |  | Metering/Mwh_today
20 | Available | Analog input | Net energy generation yesterday | 32-bit float | 19 | [5 empty] | MWh | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Low resolution | KPI | AI_0019_Net_energy_generation_yesterday_MWh |  |  | Metering/Mwh_yesterday
21 | Available | Analog input | Number of inverters online | 32-bit float | 20 | [5 empty] | count | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0020_Number_of_inverters_online_count |  |  | Stats/InvertersOnline
22 | Available | Analog input | Number of inverters available | 32-bit float | 21 | [7 empty] | -3.4028e+38 | 3.4028e+38 | [6 empty] | AI_0021_Spare
23 | Available | Analog input | Average BOM temperature | 32-bit float | 22 | [5 empty] | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0022_Average_BOM_temperature_degC
24 | Available | Analog input | Average ambient temperature | 32-bit float | 23 | [5 empty] | degC | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0023_Average_ambient_temperature_degC
25 | Available | Analog input | Average wind speed | 32-bit float | 24 | [5 empty] | m/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0024_Average_wind_speed_m_per_s
26 | Available | Analog input | Prevailing wind direction | 32-bit float | 25 | [5 empty] | degrees | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0025_Prevailing_wind_direction_degrees
27 | Available | Analog input | Average GHI irradiance | 32-bit float | 26 | [5 empty] | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0026_Average_GHI_irradiance_W_per_m2
28 | Available | Analog input | Average POA irradiance | 32-bit float | 27 | [5 empty] | W/m2 | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | KPI | AI_0027_Average_POA_irradiance_W_per_m2
29 | Available | Analog input | Average relative humidity | 32-bit float | 28 | [5 empty] | % | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0028_Average_relative_humidity_pct
30 | Available | Analog input | Average barometric pressure | 32-bit float | 29 | [5 empty] | mbar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0029_Average_barometric_pressure_mbar
31 | Available | Analog input | Average rain intensity | 32-bit float | 30 | [5 empty] | mm/hr | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | High resolution | Primary Detail | AI_0030_Average_rain_intensity_mm_per_hr
32 | Available | Analog input | Active power ramp rate feedback | 32-bit float | 31 | [5 empty] | kW/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0031_Active_power_ramp_rate_feedback_kW_per_s |  |  | Control/Active/RampRateFeedback
33 | Available | Analog input | Reactive power ramp rate feedback | 32-bit float | 32 | [5 empty] | kvar/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0032_Reactive_power_ramp_rate_feedback_kvar_per_s |  |  | Control/Reactive/RampRateFeedback
34 | Not Available | Analog input | Grid curtailment setpoint (SPARE) | 32-bit float | 33 | [5 empty] | MW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AI_0033_Grid_curtailment_setpoint_(SPARE)_MW
35 | Available | Analog output | Active power mode | 32-bit float | 0 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0000_Active_power_mode_enumeration | 0 thru 2 |  | Control/Active/ModeCommand
36 | Available | Analog output | Active power setpoint | 32-bit float | 1 | [5 empty] | MW | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0001_Active_power_setpoint_MW |  |  | Control/Active/SetpointCommand
37 | Available | Analog output | Reactive power mode | 32-bit float | 2 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0002_Reactive_power_mode_enumeration | 0 thru 3 |  | Control/Reactive/ModeCommand
38 | Available | Analog output | Voltage regulation setpoint | 32-bit float | 3 | [5 empty] | kV | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0003_Voltage_regulation_setpoint_kV |  |  | Control/Reactive/VoltageRegulationSetpointCommand
39 | Available | Analog output | Power factor regulation setpoint | 32-bit float | 4 | [5 empty] | PU | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0004_Power_factor_regulation_setpoint_PU |  |  | Control/Reactive/PFRegulationSetpointCommand
40 | Available | Analog output | Var output regulation setpoint | 32-bit float | 5 | [5 empty] | Mvar | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0005_Var_output_regulation_setpoint_Mvar |  |  | Control/Reactive/VarOutputRegulationSetpointCommand
41 | Available | Analog output | Control command source | 32-bit float | 6 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0006_Control_command_source_enumeration | 0 to 2 |  | Control/ControlCommandSourceCommand
42 | Available | Analog output | Setpoint source | 32-bit float | 7 | [5 empty] | enumeration | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0007_Setpoint_source_enumeration | 0 to 2 |  | Control/SetpointSourceCommand
43 | Available | Analog output | Active power ramp rate | 32-bit float | 8 | [5 empty] | kW/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0008_Active_power_ramp_rate_kW_per_s |  |  | Control/Active/RampRateCommand
44 | Available | Analog output | Reactive power ramp rate | 32-bit float | 9 | [5 empty] | kvar/s | 1 | -3.4028e+38 | 3.4028e+38 | -3.4028e+38 | 3.4028e+38 |  |  | Change events | KPI | AO_0009_Reactive_power_ramp_rate_kvar_per_s |  |  | Control/Reactive/RampRateCommand
45 | Available | Binary input | Primary meter communication alarm | Boolean | 0 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0000_Primary_meter_communication_alarm |  |  | Alarms/PrimaryMeterCommunicationAlarm
46 | Available | Binary input | Backup meter communication alarm | Boolean | 1 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0001_Backup_meter_communication_alarm |  |  | Alarms/BackupMeterCommunicationAlarm
47 | Available | Binary input | Backup meter in use for generation control | Boolean | 2 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0002_Backup_meter_in_use_for_generation_control |  |  | Alarms/BackupMeterInUseForGenerationControl
48 | Available | Binary input | Primary - backup meter disagreement alarm | Boolean | 3 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0003_Primary___backup_meter_disagreement_alarm |  |  | Alarms/MeterDisagreementAlarm
49 | Available | Binary input | Open loop operation alarm | Boolean | 4 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0004_Open_loop_operation_alarm |  |  | Alarms/OpenLoopOperationAlarm
50 | Not Available | Binary input | Night SVC enable feedback | Boolean | 5 |  |  | None | Enable | Disable | [10 empty] | BI_0005_Night_SVC_enable_feedback
51 | Not Available | Binary input | Cap bank PPC control enable feedback | Boolean | 6 |  |  | None | Enable | Disable | [10 empty] | BI_0006_Cap_bank_PPC_control_enable_feedback
52 | Not Available | Binary input | Cap bank in manual control | Boolean | 7 |  |  | None | Manual | Auto | [10 empty] | BI_0007_Cap_bank_in_manual_control
53 | Not Available | Binary input | Cap bank position error | Boolean | 8 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0008_Cap_bank_position_error
54 | Available | Binary input | Command source alarm | Boolean | 9 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0009_Command_source_alarm |  |  | Alarms/CommandSourceAlarm
55 | Available | Binary input | Invalid command value alarm | Boolean | 10 |  |  | On (1) | Alarm | Normal | [10 empty] | BI_0010_Invalid_command_value_alarm |  |  | Alarms/InvalidCommandValueAlarm
56 | Available | Binary input | Last setpoint source | Boolean | 11 |  |  | None | Interface | HMI | [10 empty] | BI_0011_Last_setpoint_source |  |  | Control/LastSetpointSource
57 | Not Available | Binary input | Grid curtailment flag | Boolean | 12 |  |  | None | On | Off | [10 empty] | BI_0012_Grid_curtailment_flag
58 | Not Available | Binary input | RTU permit to operate cap bank | Boolean | 13 |  |  | Off (0) | Enable | Disable | [10 empty] | BI_0013_RTU_permit_to_operate_cap_bank
59 | Available | Binary output | Plant start stop command | Boolean | 0 | LOn:LOff |  |  | Start | Stop | [10 empty] | BO_0000_Plant_start_stop_command |  |  | Control/PlantStartStopCommand
60 | Not Available | Binary output | Night SVC enable disable command | Boolean | 1 | LOn:LOff |  |  | Enable | Disable | [10 empty] | BO_0001_Night_SVC_enable_disable_command
61 | Not Available | Binary output | Cap bank PPC control enable disable command | Boolean | 2 | LOn:LOff |  |  | Enable | Disable | [10 empty] | BO_0002_Cap_bank_PPC_control_enable_disable_command
62 | Not Available | Binary output | Cap bank manual close open command | Boolean | 3 | LOn:LOff |  |  | Close | Open | [10 empty] | BO_0003_Cap_bank_manual_close_open_command
63 | Available | Binary output | Cap bank automatic control enable disable | Boolean | 4 | LOn:LOff |  |  | Auto | Manual | [10 empty] | BO_0004_Cap_bank_automatic_control_enable_disable |  |  | Control/Reactive/CapBankAutomaticControlEnableDisableCommand
64 | Available | Binary output | Emergency stop command | Boolean | 5 | LOn |  |  | Stop | [11 empty] | BO_0005_Emergency_stop_command |  |  | Control/EmergencyStopCommand
65 | Not Available | Binary output | Curtailment enable disable from grid control | Boolean | 6 | LOn:LOff |  |  | Enable | Disable | [10 empty] | BO_0006_Curtailment_enable_disable_from_grid_control
error
error
error
error
error
Note on W7: Plant Operation Status: ESTOP 0, STOPPED 1, STANDBY 2, WARMUP 3, RUN_NIGHT_SVC 4, RUN_OPEN_LOOP 5, RUN_OL_RAMP 6, RUN_CLOSED_LOOP 7, RUN_CL_RAMP 8, SHUTTING_DOWN 9
Note on W8: Active power modes: Unlimited 0 Curtailment 1 Dispatch 2
Note on W10: Reactive power modes: 0 - Off 1 - Var output regulation 2 - PF regulation 3 - AVR (voltage regulation)
Note on W14: Command/Setpoint Source: 0 - HMI only 1 - Interface only 2 - HMI and interface
Note on W15: Command/Setpoint Source: 0 - HMI only 1 - Interface only 2 - HMI and interface
Note on W41: Active power modes: Unlimited 0 Curtailment 1 Dispatch 2
Note on W43: Reactive power modes: 0 - Off 1 - Var output regulation 2 - PF regulation 3 - AVR (voltage regulation)
Note on W47: Command/Setpoint Source: 0 - HMI only 1 - Interface only 2 - HMI and interface
Note on W48: Command/Setpoint Source: 0 - HMI only 1 - Interface only 2 - HMI and interface

## Trackers to Ignition - Nexttack
Site Name | [5 empty] | Modbus |  |  | Trackers to Ignition
Last updated |  | 2023-05-29 | Device Type | Nextracker NX Horizon |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 5 | Subsystem / Zone | Trackers |  |  |  |  | How many rows per NCU can be found on the Nextracker Lookup tab
Device Register Base |  | 1 | Number of NCUs | 50 |  |  |  |  | Replace [n] with the NCU number expressed as two digits.
Register Digits |  | 6 | [6 empty] | Replace [r] with the row number expressed as three digits, up to the number of rows in the NCU
Replace [w] with the number of rows in the NCU + 1 expressed as 3 digits for weather stations and snow sensors
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Holding Register | TRK-[n] Firmware version | 32-bit signed integer | 49999 |  | 450000 |  |  |  | unitless | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
2 | Available | Holding Register | TRK-[n] NCU serial number | String | 50001 |  | 450002 |  |  |  | ASCII | 16 | [6 empty] | Not historized | Not Shown
3 | Available | Holding Register | TRK-[n] Time zone | 16-bit signed integer | 50009 |  | 450010 |  |  |  | hr | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
4 | Available | Holding Register | TRK-[n] Longitude | 64-bit signed integer | 50010 |  | 450011 |  |  |  | degrees | 1000000 | [6 empty] | Not historized | Not Shown
5 | Available | Holding Register | TRK-[n] Latitude | 64-bit signed integer | 50014 |  | 450015 |  |  |  | degrees | 1000000 | [6 empty] | Not historized | Not Shown
6 | Available | Holding Register | TRK-[n] Elevation | 32-bit signed integer | 50018 |  | 450019 |  |  |  | m | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
7 | Available | Holding Register | TRK-[n] Zigbee ID | 32-bit signed integer | 50019 |  | 450020 |  |  |  | unitless | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
8 | Available | Holding Register | TRK-[n] IP address | 32-bit unsigned integer | 50020 |  | 450021 |  |  |  | unitless | 1 | 0 | 4294967295 | 0 | 4294967295 |  |  | Not historized | Not Shown
9 | Available | Holding Register | TRK-[n] NCU UTC time second | 32-bit signed integer | 50022 |  | 450023 |  |  |  | s | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
10 | Available | Holding Register | TRK-[n] NCU UTC time minute | 32-bit signed integer | 50023 |  | 450024 |  |  |  | min | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
11 | Available | Holding Register | TRK-[n] NCU UTC time hour | 32-bit signed integer | 50024 |  | 450025 |  |  |  | hr | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
12 | Available | Holding Register | TRK-[n] NCU UTC time day | 32-bit signed integer | 50025 |  | 450026 |  |  |  | day | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
13 | Available | Holding Register | TRK-[n] NCU UTC time month | 32-bit signed integer | 50026 |  | 450027 |  |  |  | month | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
14 | Available | Holding Register | TRK-[n] NCU UTC time year | 32-bit signed integer | 50027 |  | 450028 |  |  |  | year | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
15 | Available | Holding Register | TRK-[n] AC Power Fault | 32-bit signed integer | 50028 |  | 450029 |  |  |  | enumeration | 1 | [6 empty] | Change Events | Primary Detail |  |  | Faults can be cleared by writing a 0 to this point.
16 | Available | Holding Register | TRK-[n] Global tracker state | 32-bit signed integer | 50030 |  | 450031 |  |  |  | enumeration | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Change Events | KPI |  | 0-5: R/W, 6-10: R/O
17 | Available | Holding Register | TRK-[n] SPCs and WS connected | 32-bit signed integer | 50031 |  | 450032 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Change Events | Primary Detail
18 | Available | Holding Register | TRK-[n] Wind speed | 32-bit signed integer | 50032 |  | 450033 |  |  |  | mph | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Primary Detail
19 | Available | Holding Register | TRK-[n] Water level | 32-bit signed integer | 50033 |  | 450034 |  |  |  | in | 100 | -2147483648 | 2147483647 | -21474836.48 | 21474836.47 |  |  | Low resolution | Primary Detail
20 | Available | Holding Register | TRK-[n] SPCs online | 32-bit signed integer | 50034 |  | 450035 |  |  |  | count | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Primary Detail
21 | Available | Holding Register | TRK-[n] GHI sensor | 32-bit signed integer | 50035 |  | 450036 |  |  |  | W/m2 | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Low resolution | Primary Detail
22 | Available | Holding Register | TRK-[n] Snow Level | 32-bit signed integer | 50037 |  | 450038
23 | Available | Input Register | TRK-[n] Row [r] SPC firmware version | 32-bit signed integer | [r]49 |  | 4[r]50 |  |  |  | unitless | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
24 | Available | Input Register | TRK-[n] Row [r] SPC serial number | String | [r]51 |  | 4[r]52 |  |  |  | ASCII | 16 | [6 empty] | Not historized | Not Shown
25 | Available | Holding Register | TRK-[n] Row [r] SPC fault register | 32-bit bitfield | [r]59 |  | 4[r]60 |  |  |  | unitless | 1 | [6 empty] | Change Events | Secondary Detail
26 | Available | Holding Register | TRK-[n] battery over current | Boolean | [r]59 | 0 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
27 | Available | Holding Register | TRK-[n] battery over voltage | Boolean | [r]59 | 1 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
28 | Available | Holding Register | TRK-[n] Row [r] boost over current | Boolean | [r]59 | 2 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
29 | Available | Holding Register | TRK-[n] Row [r] boost over voltage | Boolean | [r]59 | 3 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
30 | Available | Holding Register | TRK-[n] Row [r] panel over coltage | Boolean | [r]59 | 4 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
31 | Available | Holding Register | TRK-[n] Row [r] panel over current | Boolean | [r]59 | 5 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
32 | Available | Holding Register | TRK-[n] Row [r] motor over current | Boolean | [r]59 | 6 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
33 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 7 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
34 | Available | Holding Register | TRK-[n] Row [r] motor inrush over current | Boolean | [r]59 | 8 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
35 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 9 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
36 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 10 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
37 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 11 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
38 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 12 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
39 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 13 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
40 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 14 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
41 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 15 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
42 | Available | Holding Register | TRK-[n] Row [r] spc over temperature | Boolean | [r]59 | 16 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
43 | Available | Holding Register | TRK-[n] Row [r] battery over temperature | Boolean | [r]59 | 17 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
44 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 18 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
45 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 19 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
46 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 20 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
47 | Available | Holding Register | TRK-[n] Row [r] tracker stall | Boolean | [r]59 | 21 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
48 | Available | Holding Register | TRK-[n] Row [r] boost start timeout | Boolean | [r]59 | 22 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
49 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 23 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
50 | Available | Holding Register | TRK-[n] Row [r] software system error | Boolean | [r]59 | 24 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
51 | Available | Holding Register | TRK-[n] Row [r] firmware loading error | Boolean | [r]59 | 25 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
52 | Available | Holding Register | TRK-[n] Row [r] user setting loading error | Boolean | [r]59 | 26 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
53 | Available | Holding Register | TRK-[n] Row [r] tilt sensor error | Boolean | [r]59 | 27 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
54 | Available | Holding Register | TRK-[n] Row [r] motor stall | Boolean | [r]59 | 28 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
55 | Available | Holding Register | TRK-[n] Row [r] actuator fail | Boolean | [r]59 | 29 | 4[r]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
56 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 30 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
57 | Available | Holding Register | TRK-[n] Row [r] reserved | Boolean | [r]59 | 31 | 4[r]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
58 | Available | Input Register | TRK-[n] Row [r] SPC alert | 16-bit bitfield | [r]61 |  | 4[r]62 |  |  |  | unitless | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Change Events | Secondary Detail
59 | Available | Input Register | TRK-[n] Row [r] reserved | Boolean | [r]61 | 0 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
60 | Available | Input Register | TRK-[n] Row [r] reserved | Boolean | [r]61 | 1 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
61 | Available | Input Register | TRK-[n] Row [r] snow shed | Boolean | [r]61 | 2 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
62 | Available | Input Register | TRK-[n] Row [r] snow shed blackout | Boolean | [r]61 | 3 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
63 | Available | Input Register | TRK-[n] Row [r] low battery stow | Boolean | [r]61 | 4 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
64 | Available | Input Register | TRK-[n] Row [r] reserved | Boolean | [r]61 | 5 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
65 | Available | Input Register | TRK-[n] Row [r] reserved | Boolean | [r]61 | 6 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
66 | Available | Input Register | TRK-[n] Row [r] real time clock failed | Boolean | [r]61 | 7 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
67 | Available | Input Register | TRK-[n] Row [r] factory firmware | Boolean | [r]61 | 8 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
68 | Available | Input Register | TRK-[n] Row [r] invalid serial number | Boolean | [r]61 | 9 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
69 | Available | Input Register | TRK-[n] Row [r] night stow enabled | Boolean | [r]61 | 10 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
70 | Available | Input Register | TRK-[n] Row [r] wind stow enabled | Boolean | [r]61 | 11 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
71 | Available | Input Register | TRK-[n] Row [r] reserved | Boolean | [r]61 | 12 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
72 | Available | Input Register | TRK-[n] Row [r] flood stow enabled | Boolean | [r]61 | 13 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
73 | Available | Input Register | TRK-[n] Row [r] snow stow enabled | Boolean | [r]61 | 14 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
74 | Available | Input Register | TRK-[n] Row [r] reserved | Boolean | [r]61 | 15 | 4[r]62 | On (1) | Alarm | Normal | boolean | [7 empty] | Not historized | Not Shown
75 | Available | Input Register | TRK-[n] Row [r] SPC status | 16-bit bitfield | [r]62 |  | 4[r]63 |  |  |  | unitless | 1 | [7 empty] | Secondary Detail
76 | Available | Input Register | TRK-[n] Row [r] Battery charger status | 8-bit unsigned integer | [r]62 | 0-7 | 4[r]63 |  |  |  | enumeration | [10 empty] | 0-6 | Status register & 255 gives bits 0-7 as an int
77 | Available | Input Register | TRK-[n] Row [r] Tracker status | 8-bit unsigned integer | [r]62 | 8-15 | 4[r]63 |  |  |  | enumeration | [10 empty] | 0-1 | Status register >> 8 gives bit 8-15 as an int
78 | Available | Input Register | TRK-[n] Row [r] target angle | 16-bit signed integer | [r]63 |  | 4[r]64 |  |  |  | degrees | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  | Low resolution | Secondary Detail
79 | Available | Input Register | TRK-[n] Row [r] tracker position | 16-bit signed integer | [r]64 |  | 4[r]65 |  |  |  | degrees | 100 | -32768 | 32767 | -327.68 | 327.67 |  |  | Low resolution | Secondary Detail
80 | Available | Holding Register | TRK-[n] Row [r] automatic tracking | 16-bit signed integer | [r]65 |  | 4[r]66 | None | Enabled | Disabled | boolean | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Low resolution | Secondary Detail
81 | Available | Input Register | TRK-[n] Row [r] SPC time second | 16-bit signed integer | [r]66 |  | 4[r]67 |  |  |  | s | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
82 | Available | Input Register | TRK-[n] Row [r] SPC time minute | 16-bit signed integer | [r]67 |  | 4[r]68 |  |  |  | min | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
83 | Available | Input Register | TRK-[n] Row [r] SPC time hour | 16-bit signed integer | [r]68 |  | 4[r]69 |  |  |  | hr | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
84 | Available | Input Register | TRK-[n] Row [r] SPC time day | 16-bit signed integer | [r]69 |  | 4[r]70 |  |  |  | day | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
85 | Available | Input Register | TRK-[n] Row [r] SPC time month | 16-bit signed integer | [r]70 |  | 4[r]71 |  |  |  | month | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
86 | Available | Input Register | TRK-[n] Row [r] SPC time year | 16-bit signed integer | [r]71 |  | 4[r]72 |  |  |  | year | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
87 | Available | Input Register | TRK-[n] Row [r] device online | 16-bit signed integer | [r]72 |  | 4[r]73 |  |  |  | enumeration | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Change Events | Secondary Detail
88 | Available | Input Register | TRK-[n] Row [r] name | 16-bit signed integer | [r]73 |  | 4[r]74 |  |  |  | unitless | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
89 | Available | Holding Register | TRK-[n] weather station firmware version | 32-bit signed integer | [w]49 |  | 4[w]50 |  |  |  | unitless | 1 | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
90 | Available | Holding Register | TRK-[n] weather station serial number | String | [w]51 |  | 4[w]52 |  |  |  | ASCII | 16 | [6 empty] | Not historized | Not Shown
91 | Available | Holding Register | TRK-[n] weather station fault register | 32-bit bitfield | [w]59 |  | 4[w]60 |  |  |  | unitless | 1 | [6 empty] | Change Events | Secondary Detail |  |  | Faults can be cleared by writing a 0 to this point.
92 | Available | Holding Register | TRK-[n] WS [w] battery over current | Boolean | [w]59 | 0 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
93 | Available | Holding Register | TRK-[n] WS [w] battery over voltage | Boolean | [w]59 | 1 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
94 | Available | Holding Register | TRK-[n] WS [w] boost over current | Boolean | [w]59 | 2 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
95 | Available | Holding Register | TRK-[n] WS [w] boost over voltage | Boolean | [w]59 | 3 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
96 | Available | Holding Register | TRK-[n] WS [w] panel over coltage | Boolean | [w]59 | 4 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
97 | Available | Holding Register | TRK-[n] WS [w] panel over current | Boolean | [w]59 | 5 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
98 | Available | Holding Register | TRK-[n] WS [w] motor over current | Boolean | [w]59 | 6 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
99 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 7 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
100 | Available | Holding Register | TRK-[n] WS [w] motor inrush over current | Boolean | [w]59 | 8 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
101 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 9 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
102 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 10 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
103 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 11 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
104 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 12 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
105 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 13 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
106 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 14 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
107 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 15 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
108 | Available | Holding Register | TRK-[n] WS [w] spc over temperature | Boolean | [w]59 | 16 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
109 | Available | Holding Register | TRK-[n] WS [w] battery over temperature | Boolean | [w]59 | 17 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
110 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 18 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
111 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 19 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
112 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 20 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
113 | Available | Holding Register | TRK-[n] WS [w] tracker stall | Boolean | [w]59 | 21 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
114 | Available | Holding Register | TRK-[n] WS [w] boost start timeout | Boolean | [w]59 | 22 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
115 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 23 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
116 | Available | Holding Register | TRK-[n] WS [w] software system error | Boolean | [w]59 | 24 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
117 | Available | Holding Register | TRK-[n] WS [w] firmware loading error | Boolean | [w]59 | 25 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
118 | Available | Holding Register | TRK-[n] WS [w] user setting loading error | Boolean | [w]59 | 26 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
119 | Available | Holding Register | TRK-[n] WS [w] tilt sensor error | Boolean | [w]59 | 27 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
120 | Available | Holding Register | TRK-[n] WS [w] motor stall | Boolean | [w]59 | 28 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
121 | Available | Holding Register | TRK-[n] WS [w] actuator fail | Boolean | [w]59 | 29 | 4[w]60 | On (1) | Alarm | Normal | unitless | [7 empty] | Not historized | Not Shown
122 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 30 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
123 | Available | Holding Register | TRK-[n] WS [w] reserved | Boolean | [w]59 | 31 | 4[w]60 |  |  |  | unitless | [7 empty] | Not historized | Not Shown
124 | Available | Holding Register | TRK-[n] weather station alert | 16-bit signed integer | [w]61 |  | 4[w]62 | On (1) | Alarm | Normal | boolean | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Change Events | Secondary Detail
125 | Available | Holding Register | TRK-[n] weather station status | 16-bit bitfield | [w]62 |  | 4[w]63 |  |  |  | unitless | 1 | [6 empty] | Change Events | Secondary Detail
126 | Available | Input Register | TRK-[n] weather station time second | 16-bit signed integer | [w]66 |  | 4[w]67 |  |  |  | s | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
127 | Available | Input Register | TRK-[n] weather station time minute | 16-bit signed integer | [w]67 |  | 4[w]68 |  |  |  | min | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
128 | Available | Input Register | TRK-[n] weather station time hour | 16-bit signed integer | [w]68 |  | 4[w]69 |  |  |  | hr | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
129 | Available | Input Register | TRK-[n] weather station time day | 16-bit signed integer | [w]69 |  | 4[w]70 |  |  |  | day | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
130 | Available | Input Register | TRK-[n] weather station time month | 16-bit signed integer | [w]70 |  | 4[w]71 |  |  |  | month | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
131 | Available | Input Register | TRK-[n] weather station time year | 16-bit signed integer | [w]71 |  | 4[w]72 |  |  |  | year | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
132 | Available | Input Register | TRK-[n] weather station device online | 16-bit signed integer | [w]72 |  | 4[w]73 |  |  |  | enumeration | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Change Events | Secondary Detail
133 | Available | Input Register | TRK-[n] weather station name | 16-bit signed integer | [w]73 |  | 4[w]74 |  |  |  | unitless | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
134 | Available | Input Register | TRK-[n] weather station water level | 16-bit signed integer | [w]74 |  | 4[w]75 |  |  |  | in | 0.01 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
135 | Available | Input Register | TRK-[n] weather station snow height | 16-bit signed integer | [w]75 |  | 4[w]76 |  |  |  | in | 0.01 | [6 empty] | Not historized | Not Shown
136 | Available | Input Register | TRK-[n] weather station wind speed | 16-bit signed integer | [w]76 |  | 4[w]77 |  |  |  | mph | 0.01 | [6 empty] | Not historized | Not Shown

## Trackers to Ignition - Nevados
Site Name | [5 empty] | Modbus |  |  | Trackers to Ignition
Last updated |  | 2023-05-29 | Device Type | Nevados |  |  |  |  | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 5 | Subsystem / Zone | Trackers |  |  |  |  | How many rows per NCU can be found on the Nextracker Lookup tab
Device Register Base |  | 0 | Number of ZCs | 31 |  |  |  |  | Replace [n] with the NCU number expressed as two digits.
Register Digits |  | 5 | [6 empty] | Replace [r] with the row number expressed as three digits, up to the number of rows in the NCU
Replace [w] with the number of rows in the NCU + 1 expressed as 3 digits for weather stations and snow sensors
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments
1 | Available | Coil | Force Update | Boolean | 0 |  | 0 |  | Force Update | Normal | unitless |  | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
2 | Available | Discrete Input | Update Status | Boolean | 0 |  | 10000 |  | Currently Updating | Normal | unitless | [7 empty] | Not historized | Not Shown
3 | Available | Input Register | Row [r] Alarm Bitfield | 32-bit bitfield | [r]-1 |  | 29999+[r] |  |  |  | unitless | 1 | -32768 | 32767 | -32768 | 32767 |  |  | Not historized | Not Shown
4 | Available | Input Register | Row[r] Motor Fault | Boolean | [r]-1 | 0 | 29999+[r] | On (1) | Alarm | Normal | [8 empty] | Not historized | Not Shown
5 | Available | Input Register | Row[r] Position Error | Boolean | [r]-1 | 1 | 29999+[r] | On (1) | Alarm | Normal | [8 empty] | Not historized | Not Shown
6 | Available | Input Register | Row[r] Sensor Error | Boolean | [r]-1 | 2 | 29999+[r] | On (1) | Alarm | Normal |  |  | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
7 | Available | Input Register | Row[r] Comms Error | Boolean | [r]-1 | 3 | 29999+[r] | On (1) | Alarm | Normal |  |  | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
8 | Available | Input Register | Row[r] Low Battery | Boolean | [r]-1 | 4 | 29999+[r] | On (1) | Alarm | Normal |  |  | 0 | 4294967295 | 0 | 4294967295 |  |  | Not historized | Not Shown
9 | Available | Input Register | Row[r] Uncomissioned | Boolean | [r]-1 | 15 | 29999+[r] | On (1) | Alarm | Normal |  |  | -2147483648 | 2147483647 | -2147483648 | 2147483647 |  |  | Not historized | Not Shown
10 | Available | Input Register | Row [r] Mode Enumeration | 16-bit unsigned integer | [r]+179 |  | 30179+[r] |  |  |  | unitless | 1 | [6 empty] | Change Events
11 | Available | Input Register | Row [r] Position Angle | 16-bit unsigned integer | [r]+359 |  | 30359+[r] |  |  |  | deg | 0.01 | [6 empty] | Low resolution
12 | Available | Holding Register | Row [r] Mode Command | 16-bit unsigned integer | [r] |  | 40000 + [r] |  |  |  | unitless | 1 | [6 empty] | Low resolution
13 | Available | Holding Register | Row [r] Position Command | 16-bit unsigned integer | [r]+359 |  | 30359+[r] |  |  |  | deg | 0.01 | [6 empty] | Low resolution
Note on X17: Matt Munin: Name Code Description Normal Tracking 0x0001 Automatic movement to scheduled pitch Wind Stow 0x0002 Automatic movement to wind stow pitch Wind Stow 0x0003 Automatic movement to wind stow pitch Flat 0x0004 Automatic movement to flat pitch Manual Control 0x0005 No automatic movement but move commands accepted East 0x0006 Automatic movement to maximum East pitch West 0x0007 Automatic movement to maximum West pitch Normal Tracking: Wind Stow 0x0110 Automatic movement to wind stow pitch due to high winds Normal Tracking: Snow Stow 0x0120 Automatic movement to wind stow pitch due to snow

## Battery Monitors to Ignition
Site Name | [5 empty] | Modbus |  |  |  | Battery Monitors to Ignition
Last updated |  | 2023-06-28 | Device Type | Victron MPPT 75/10 | [5 empty] | The scalar is the multiplier to put the actual measurement value on the wire, and the divisor to take the actual measurement value off the wire.
Index digits in name |  | 5 | Subsystem / Zone | SCADA System
Device Register Base |  | 1 | Modbus Server ID | 226 | [5 empty] | Replace [n] with the skid number expressed as minimal digits
Register Digits |  | 6 | [7 empty] | Replace [n2] with the skid number expressed as two digits
List Index | Availability | Modbus Table | Point Description | Data Type | RTAC Modbus index | Modbus Bit | Modbus Register | Alarm State | On (1) State | Off (0) State | Units | Scalar | Min Count | Max Count | Min Value | Max Value | Analog Alarm Limits | Alarm Profile | Historian Profile | HMI Category | RTAC Point Name | Enumeration Table | Comments | Ignt TagPath Prefix: [GarnetMesaSolar]Network/ | Column1
1 | Available | Holding Register | 30BAT-[n] Battery voltage | 16-bit unsigned integer | 771 |  | 400772 |  | Analog |  | V |  | 100 | 0 | 65535 | 0 | 655.35 | 22.5,23,28.4,29.4 | 5-State | Low resolution | Diagnostic |  |  |  | X
2 | Available | Holding Register | 30BAT-[n] Battery current | 16-bit signed integer | 772 |  | 400773 |  |  |  | A |  | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  | Low resolution | Diagnostic |  |  |  | FieldEnclosure[n]/30BatS[n2]/Ibatt
3 | Available | Holding Register | 30BAT-[n] Charger on/off | 16-bit unsigned integer | 774 |  | 400775 |  |  |  | enumeration |  | 1 | 0 | 65535 | 0 | 65535 |  |  | Change events | Diagnostic | 1,4
4 | Available | Holding Register | 30BAT-[n] Charge state | 16-bit unsigned integer | 775 |  | 400776 |  | Analog |  | enumeration |  | 1 | 0 | 65535 | 0 | 65535 | 2 | Value | Change events | Diagnostic | 0, 2 thru 7, 11, 252 |  |  | FieldEnclosure[n]/30BatS[n2]/ChargeStateCode
5 | Available | Holding Register | 90BAT-[n] PV voltage | 16-bit unsigned integer | 776 |  | 400777 |  |  |  | V |  | 100 | 0 | 65535 | 0 | 655.35 |  |  | Low resolution | Diagnostic |  |  |  | FieldEnclosure[n]/30BatS[n2]/Vpv
6 | Available | Holding Register | 30BAT-[n] PV current | 16-bit signed integer | 777 |  | 400778 |  |  |  | A |  | 10 | -32768 | 32767 | -3276.8 | 3276.7 |  |  | Low resolution | Diagnostic |  |  |  | FieldEnclosure[n]/30BatS[n2]/Ipv
7 | Available | Holding Register | 30BAT-[n] Yield today | 16-bit unsigned integer | 784 |  | 400785 |  |  |  | kWh |  | 10 | 0 | 65535 | 0 | 6553.5 |  |  | Low resolution | Diagnostic
8 | Available | Holding Register | 30BAT-[n] Maximum charge power today | 16-bit unsigned integer | 785 |  | 400786 |  |  |  | W |  | 1 | 0 | 65535 | 0 | 65535 |  |  | Low resolution | Diagnostic
9 | Available | Holding Register | 30BAT-[n] Yield yesterday | 16-bit unsigned integer | 786 |  | 400787 |  |  |  | kWh |  | 10 | 0 | 65535 | 0 | 6553.5 |  |  | Low resolution | Diagnostic |  |  |  | FieldEnclosure[n]/30BatS[n2]/kWhYesterday
10 | Available | Holding Register | 30BAT-[n] Maximum charge power yesterday | 16-bit unsigned integer | 787 |  | 400788 |  |  |  | W |  | 1 | 0 | 65535 | 0 | 65535 |  |  | Low resolution | Diagnostic |  |  |  | FieldEnclosure[n]/30BatS[n2]/PmaxYesterday
11 | Available | Holding Register | 30BAT-[n] Error code | 16-bit unsigned integer | 788 |  | 400789 |  | Analog |  | enumeration |  | 1 | 0 | 65535 | 0 | 65535 | n/a,0,0,n/a | Out of band | Change events | Diagnostic
12 | Available | Holding Register | 30BAT-[n] PV power | 16-bit unsigned integer | 789 |  | 400790 |  |  |  | W |  | 10 | 0 | 65535 | 0 | 6553.5 |  |  | Low resolution | Diagnostic | 0 thru 9, 17 thru 20, 22, 23, 34 |  |  | FieldEnclosure[n]/30BatS[n2]/Ppv
13 | Available | Holding Register | 30BAT-[n] User yield | 16-bit unsigned integer | 790 |  | 400791 |  |  |  | kWh |  | 10 | 0 | 65535 | 0 | 6553.5 |  |  | Low resolution | Diagnostic
14 | Available | Holding Register | 30BAT-[n] MPP operation mode | 16-bit unsigned integer | 791 |  | 400792 |  |  |  | enumeration |  | 1 | 0 | 65535 | 0 | 65535 |  |  | Change events | Diagnostic | 0 thru 2, 255 |  |  | FieldEnclosure[n]/30BatS[n2]/MPPTmodeCode
Note on W10: Charger Mode: 1 - On 4 - Off
Note on W11: Charge State: 0 - OFF 2 - Fault 3 - Bulk 4 - Absorbtion 5 - Float 6 - Storage 7 - Equalize 11 - Other 252 - External control
Note on W19: Error Codes: 0=No error; 1=Battery temperature too high; 2=Battery voltage too high; 3=Battery temperature sensor miswired (+); 4=Battery temperature sensor miswired (-); 5=Battery temperature sensor disconnected; 6=Battery voltage sense miswired (+); 7=Battery voltage sense miswired (-); 8=Battery voltage sense disconnected; 9=Battery voltage wire losses too high; 17=Charger temperature too high; 18=Charger over-current; 19=Charger current polarity reversed; 20=Bulk time limit reached; 22=Charger temperature sensor miswired; 23=Charger temperature sensor disconnected; 34=Input current too high
Note on W21: MPPT Mode: 0 - OFF 1 - Voltage/Current Limited 2 - MPPT 255 - Not Available

## Lookups
Lookup tables
Input type | Abbreviation |  | Data Type | Min Count | Max Count | Units | DNP3 variations | Invalid DNP Object
Analog input | AI_ |  | 16-bit signed integer | -32768 | 32767 | A | Analog Input | Binary Input | Analog Output | Binary Output | Counter
Analog output | AO_ |  | 16-bit unsigned integer | 0 | 65535 | V | 16-bit signed integer | Boolean | 16-bit signed integer | Boolean | 16-bit unsigned integer
Binary input | BI_ |  | 32-bit float | -3.4028e+38 | 3.4028e+38 | kV | 32-bit signed integer |  | 32-bit signed integer |  | 32-bit unsigned integer
Binary output | BO_ |  | 32-bit signed integer | -2147483648 | 2147483647 | W | 32-bit float |  | 32-bit float |  | 16-bit bitfield
Counter | CNT_ |  | 32-bit unsigned integer | 0 | 4294967295 | kW |  |  |  |  | 32-bit bitfield
Coil | COIL_ | 0 |  |  |  | MW
Discrete input | DI_ | 1 | Binary | Boolean |  | Wh
Holding register | HREG_ | 4 | 0 | False |  | kWh
Input register | IREG_ | 3 | 1 | True |  | MWh
|  |  | - | N/A |  | var
Analog input | 32 bit float |  |  |  |  | kvar
Binary input | Boolean |  |  |  |  | Mvar
varh
kvarh
State | Verb past tense |  |  |  |  | Mvarh
Alarm | Alarmed |  |  |  |  | VA
Closed | Closed |  |  |  |  | kVA
Disabled | Disabled |  |  |  |  | MVA
Enabled | Enabled |  |  |  |  | Hz
Locked out | Locked out |  |  |  |  | %
Normal | Returned to normal |  |  |  |  | PU
Offline | Went offline |  |  |  |  | degC
Online | Came online |  |  |  |  | degF
Open | Opened |  |  |  |  | unitless
Reset | Reset |  |  |  |  | ppm
Tripped | Tripped |  |  |  |  | m/s
mph
bar
mbar
kPa
degrees
W/m2
mm
mm/hr
kg
hr
min
s
count
boolean